## Slide 1: Agenda
UNECE Convention on Long-range Transboundary Air Pollution
General cost methodology
Calculation of boiler outlet emission loads
Economic assessment of DeNOx technologies
Economic assessment of dedusting technologies
Economic assessment of DeSOx technologies

## Slide 2
UNECE Convention on Long-range Transboundary Air Pollution
Economic assessment of Dedusting technologies
IED ELVs and Dust emission issues in coal power plant
Existing plants |  | New plants | 
Power (MW) | ELV (mg/Nm3) | Power (MW) | ELV (mg/Nm3)
50-100 | 30 | 50-300 | 20
100-300 | 25 |  | 
>300 | 20 | >300 | 10

## Slide 3
UNECE Convention on Long-range Transboundary Air Pollution
Economic assessment of Dedusting technologies
Specific cost methodology for Deduster
Adapted methodogy from US EPA Air pollution cost control manual
Variable operating cost
 | Fabric Filter | Electrostatic Precipitator
Cequip | 1.Baghouse compartments 2.Bags 3.Cages | General equipment
 | 0.74 | 0.67
 | 0.45 | 0.57
Cop,var | 1.Bag replacement 2.Compressed air consumption 3. Fan consumption | 1.ESP power requirement 2.Fan consumption 3. SO3 consumption
Investment cost

## Slide 4
UNECE Convention on Long-range Transboundary Air Pollution
Economic assessment of Dedusting technologies
Pulse Jet Fabric Filter

## Slide 5: General approach for Pulse Jet Fabric Filter equipment cost
UNECE Convention on Long-range Transboundary Air Pollution
Logic Tree
Economic assessment of Dedusting technologies

## Slide 6: Total filtration area calculation and industrial example
UNECE Convention on Long-range Transboundary Air Pollution
Economic assessment of Dedusting technologies
Industrial example from Termokimik1
  Power 660 MWe => 1,650 MWth
  Volumetric flow gas = 1,750,000 Nm3/h
  A/C = 1.11 cm/s
  ANC = 45,900 m2
  AGC = 47,736 m2
  16 compartments => Acomp = 2,984 m2
1Available online : http://www.termokimik.it/pdf/torrevaldaliga_eng.pdf

## Slide 7: Cost comparison for Pulse Jet Fabric Filter units Variable input parameters and comparison with literature data
UNECE Convention on Long-range Transboundary Air Pollution
Economic assessment of Dedusting technologies
Parameter | Value
A/C (m/s) | 1.8e-2
Number of compartments | Division made in order to get Acomp = 2,500 m2
Number of extra-compartments | Bettween 0 and 2
Compartement baghouse | Stainless steel Insulated
Filtering media | RT
Reference price for PE media (€) | 9
Bag dimension | Lenght : 8m Diameter : 150 mm
Cage price (€/m2) | 20
Chart: Power (MWth)
| 250 | 500 | 750 | 1000 | 1250 | 1500 | 1750 | 2000
EGTEI Model | 6025.7082 | 11840.4162 | 19020.3304 | 24693.4963 | 30481.6371 | 37871.742 | 43617.461 | 49386.43
RAINS | 4093.3924 | 8186.7848 | 12280.1772 | 16373.5695 | 20466.9619 | 24560.3543 | 28653.7467 | 32747.1391
AEP | 4815.7557 | 9631.5115 | 14447.2672 | 19263.023 | 24078.7787 | 28894.5345 | 33710.2902 | 38526.046
Nalbandian [Smith] | 5837.1857 | 11674.3713 | 17511.557 | 23348.7427 | 29185.9284 | 35023.114 | 40860.2997 | 46697.4854
Naldandian [Orfanoudakis] | 5310.5223 | 10621.0446 | 15931.5669 | 21242.0892 | 26552.6115 | 31863.1338 | 37173.6561 | 42484.1784
Nalbandian | 5266.6337 | 10533.2674 | 15799.9011 | 21066.5348 | 26333.1684 | 31599.8021 | 36866.4358 | 42133.0695
World bank | 5608.3014 | 11216.6027 | 16824.9041 | 22433.2054 | 28041.5068 | 33649.8081 | 39258.1095 | 44866.4108
IEA | 7568.8885 | 15137.777 | 22706.6655 | 30275.554 | 37844.4425 | 45413.331 | 52982.2195 | 60551.108
Balcke Durr | 4869.9948 | 9739.9896 | 14609.9844 | 19479.9791 | 24349.9739 | 29219.9687 | 34089.9635 | 38959.9583
PM BART determination [American Electric Power] | 9558.2068 | 19116.4135 | 28674.6203 | 38232.8271 | 47791.0339 | 57349.2406 | 66907.4474 | 76465.6542
Sergent et Lundy | 5487.1521 | 10974.3043 | 16461.4564 | 21948.6085 | 27435.7606 | 32922.9128 | 38410.0649 | 43897.217
IEA | 9415.7492 | 18831.4984 | 28247.2476 | 37662.9967 | 47078.7459 | 56494.4951 | 65910.2443 | 75325.9935

## Slide 8: Air to Cloth ratio influence and industrial values
UNECE Convention on Long-range Transboundary Air Pollution
Economic assessment of Dedusting technologies
Industrial example | Air to cloth ratio (m/s)
Termokimik | 0.011
Balcke Dürr | 0.014
GE Energy | 0.014 – 0.017
Lurgi | 0.014 – 0.0167
Otter Tail Power Company | 0.0172
For a 1000 MWth combustion plant

## Slide 9: Operating Cost for Pulse Jet Fabric Filter and Efficiency
UNECE Convention on Long-range Transboundary Air Pollution
Economic assessment of Dedusting technologies

## Slide 10: Operating Cost for Pulse Jet Fabric Filter
UNECE Convention on Long-range Transboundary Air Pollution
Economic assessment of Dedusting technologies
Specific dust reduction cost = total cost per year / dust emission saved per year
Utility electricity cost : Fan consumption and comrpessed air consumption
Bag replacement : assuming 20,000 hours of bag lifetime

## Slide 11: Electrostatic Precipitator
UNECE Convention on Long-range Transboundary Air Pollution
Economic assessment of Dedusting technologies

## Slide 12: General approach for ESP equipment cost
UNECE Convention on Long-range Transboundary Air Pollution
Logic Tree
Economic assessment of Dedusting technologies

## Slide 13: Effective collecting plate area determination from method 2
UNECE Convention on Long-range Transboundary Air Pollution
Economic assessment of Dedusting technologies
SCA1
AECP,1
SCAn
AECP,n
k = 1
k = n
MMD1=MMDin
MMDn
Chart: Particle Size Distribution
| 1.2 | 2.2999999999999998 | 4 | 5.4 | 8.6 | 13 | 35
Cumulative mass fraction | 0.005 | 0.06 | 0.34 | 0.6 | 0.9 | 0.98 | 1
 | 0.5
n = number of ESP fields

## Slide 14: Evolution of SCA as a function of MMDin and T
UNECE Convention on Long-range Transboundary Air Pollution
Economic assessment of Dedusting technologies
Chart: SCA = f ( MMDin and T)
| 1 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100
400 | 420.8402 | 230.1708 | 191.0435 | 171.4617 | 158.398 | 148.6131 | 140.8052 | 134.3201 | 128.7825 | 123.957 | 119.6862 | 115.8596 | 112.3968 | 109.2374 | 106.3347 | 103.6522 | 101.1606 | 98.8358 | 96.6584 | 94.6118 | 92.6823
450 | 674.8991 | 369.1236 | 306.3754 | 274.9722 | 254.0221 | 238.33 | 225.8085 | 215.4084 | 206.5278 | 198.7891 | 191.94 | 185.8034 | 180.2501 | 175.1834 | 170.5284 | 166.2265 | 162.2306 | 158.5025 | 155.0105 | 151.7285 | 148.6342
500 | 1029.7372 | 563.1957 | 467.4567 | 419.5428 | 387.5779 | 363.6355 | 344.5306 | 328.6625 | 315.1128 | 303.3054 | 292.8553 | 283.4922 | 275.0193 | 267.2886 | 260.1863 | 253.6226 | 247.5257 | 241.8374 | 236.5095 | 231.5019 | 226.7807
550 | 1509.0758 | 825.3611 | 685.056 | 614.8383 | 567.9938 | 532.9064 | 504.9082 | 481.6536 | 461.7966 | 444.4929 | 429.1783 | 415.4567 | 403.0397 | 391.7104 | 381.3019 | 371.6829 | 362.748 | 354.4118 | 346.6038 | 339.2651 | 332.3463
600 | 2139.1596 | 1169.9738 | 971.0871 | 871.5515 | 805.1481 | 755.4105 | 715.7223 | 682.7582 | 654.6103 | 630.0819 | 608.3729 | 588.9222 | 571.3207 | 555.2611 | 540.5068 | 526.8715 | 514.206 | 502.3892 | 491.3211 | 480.9184 | 471.1107
650 | 2948.7587 | 1612.769 | 1338.6106 | 1201.4041 | 1109.8692 | 1041.3077 | 986.5988 | 941.159 | 902.358 | 868.5464 | 838.6214 | 811.8092 | 787.5461 | 765.4086 | 745.0702 | 726.2744 | 708.8155 | 692.5265 | 677.2695 | 662.9296 | 649.41
T (K)
CUECost workbook : 50 s/m < SCA <190 s/m
Schwarze Pumpe: SCA =117.4 s/m [Balcke Dürr]
Waigaoqiao : SCA = 85.6 s/m [Balcke Dürr]
Baclke Dürr : SCA = 226 s/m

## Slide 15: Cost comparison for ESP units Variable input parameters and comparison with literature data
UNECE Convention on Long-range Transboundary Air Pollution
Economic assessment of Dedusting technologies
Parameter | Range choice
Efficiency [η] (%) | 99.89
Temperature [T] (K) | 400
Mass Mean diameter [MMDin] (µm) | 12
ESP specific equipment | Yes
ESP material | Stainless steel 304
SO3 injection precaution | Yes
Chart: Power (MWth)
| 250 | 500 | 750 | 1000 | 1250 | 1500 | 1750 | 2000
EGTEI Model | 7388.8826 | 13467.2862 | 19146.3519 | 24583.7031 | 29849.6197 | 34983.7476 | 40011.4257 | 44950.1802
RAINS | 2975.4491 | 5950.8982 | 8926.3473 | 11901.7964 | 14877.2454 | 17852.6945 | 20828.1436 | 23803.5927
AEP | 5847.7034 | 11695.4068 | 17543.1102 | 23390.8136 | 29238.5171 | 35086.2205 | 40933.9239 | 46781.6273
Nalbandian | 6205.85 | 12411.7001 | 18617.5501 | 24823.4001 | 31029.2502 | 37235.1002 | 43440.9502 | 49646.8002
Naldandian [Orfanoudakis] | 7461.0644 | 14922.1288 | 22383.1932 | 29844.2576 | 37305.322 | 44766.3864 | 52227.4508 | 59688.5151
World bank | 4829.3706 | 9658.7412 | 14488.1118 | 19317.4824 | 24146.8531 | 28976.2237 | 33805.5943 | 38634.9649
IEA | 6307.4071 | 12614.8142 | 18922.2212 | 25229.6283 | 31537.0354 | 37844.4425 | 44151.8496 | 50459.2566
Balcke Durr | 8088.7383 | 16177.4765 | 24266.2148 | 32354.9531 | 40443.6913 | 48532.4296 | 56621.1679 | 64709.9062
Questionnary Plant D | 5832.5159 | 11665.0318 | 17497.5478 | 23330.0637 | 29162.5796 | 34995.0955 | 40827.6115 | 46660.1274
Zevenhoven & Kilpinen | 4319.5499 | 8639.0998 | 12958.6498 | 17278.1997 | 21597.7496 | 25917.2995 | 30236.8494 | 34556.3994
Rubin | 9579.9828 | 19159.9657 | 28739.9485 | 38319.9314 | 47899.9142 | 57479.8971 | 67059.8799 | 76639.8628
Sankey | 5964.0624 | 11928.1249 | 17892.1873 | 23856.2498 | 29820.3122 | 35784.3746 | 41748.4371 | 47712.4995

## Slide 16: Operating Cost for ESP units
UNECE Convention on Long-range Transboundary Air Pollution
Economic assessment of Dedusting technologies
Specific dust reduction cost = total cost per year / dust emission saved per year
Utility electricity cost : Fan consumption and ESP power requirement
SO3 consumption : assuming precaution injection at 35 kg/h