## Explanation
Colour Guide
Results
Input Data
Input data for the plant to be tested |  | Sheet to be filled with data
For a plant using coal and or biomass |  | Sheet Solid fuels - emission calc.
For a plant using heavy fuel oil |  | Sheet Liquid fuels - emission calc.
For a plant using natural gas |  | Sheet Natural gas - emission calc.
Results |  | Sheet to be filled for parameters characterising the reduction technique
and results of cost estimation
Costs of DeNOx techniques for plant using coal and biomass |  | Solid fuels - NOx Analysis
Costs of DeNOx techniques for plant using heavy fuel oil |  | Liquid fuels - NOx Analysis
Costs of DeNOx techniques for plant using natural gas |  | Natural gas - NOx Analysis
Costs of fabric filters for plant using coal and biomass |  | Solid fuels_Fabric_Filter
Costs of ESP for plant using coal and biomass |  | Solid fuels_ESP
Costs of ESP for plant using heavy fuel oil |  | Liquid fuels_ESP
Costs of LSFO FGD and LSD FGD for plants using coal and biomass |  | Solid fuels_DeSO2
Costs of DSI FGD for plants using coal and biomass |  | Solid fuels_DeSO2 + Solid fuel_Fabric_Filter DSI
Costs of LSFO FGD and LSD FGD for plants using heavy fuel oils |  | Liquid fuels_DeSO2
Costs of DSI FGD for plants using heavy fuel oils |  | Liquid fuels_DeSO2 + Liquid fuel_Fabric_Filter DSI
How to use the file :
Step 1
Start to fill in the characteristics of the plant to be tested and fuels used in this plant
For coal, biomass and heavy fuel oil plants | For natural gas plants
Thermal Capacity [bsth]
Gross Electric Efficiency [ηgross]
NOx boiler outlet emissions [loadboNOx,dry,O2ref]
Biomass co-firng (not with heavy fuel oil)
Boiler characteristics
Capacity Factor (full load hours)
Use of Broad or detailed characteristics of fuels
Broad coal composition or detailed coal composition
Broad coal composition or detailed coal composition
Reference O2 content
fixed O&M costs in %
Depreciation time
Interest rate
Step 2
Continue with the sheet of results adapted to the case to be tested.
Fill requested data appearing in blue cells. Data requested different from technique to technique
Observe the results in green cells.

## Solid fuels - emission calc.
Basic Assumptions
Colour Guide |  |  | Parameter | Value | Unit | Parameter | Value | Unit
Results |  |  | Ref. O2 content [O2,ref.] | 6 | %-Vol. | Depreciation time | 15 | years
Input Data |  |  | Fixed O&M Costs | 2% | of total Investment | Interest rate | 4% | % p. a.
[6 empty] | Capital Recovery Factor | 8.994% | % p. a.
Chemical Data | [9 empty] | Chemical Data - Reference Boxes
Molar masses Mi [kg/kmol]
Elements |  | Substances |  |  | Factors
S | 32.06 | SO2 | 64.06 |  | Mass density of air [δair] | 1.2 | kg/Nm³
N | 14 | NOx (as NO2) | 44 |  | Spec. Ideal gas volume | 22.414 | Nm³/kmol
C | 12 | CO2 | 44
O | 16 | NH3 | 17
Ca | 40 | Urea | 60
H | 1 | CaSO4 x 2 H2O | 172.06
|  | CaCO3 | 100
|  | H2O | 18
Plant Characteristics | [9 empty] | Plant Characteristics - Reference Boxes
Thermal Capacity [bsth] | 1250 | MWth | [7 empty] | NOx Boiler outlet emissions according to technology [mg/Nm³]
Gross Electric Efficiency [ηgross] | 40 | % (LHV) | [7 empty] | Boilers and Process Heaters
[11 empty] | Hard Coal / Bituminous Coal |  | Lignite
Please enter the appropriate NOx boiler outlet emission concentration | [10 empty] | Wall-Fired | Tangentially-Fired | Wall-Fired | Tangentially-Fired
NOx boiler outlet emissions [loadboNOx,dry,O2ref] | 600 | mg/Nm³ NOx, dry, ref O2-% | [7 empty] | 1st Gen. LNB | 600-800 | 500-600 | 300-400 | 300-400
For guidance, see Reference Box | [9 empty] | 2nd Gen. LNB | 500-600 | 400-500 | 200-300 | 200-300
[10 empty] | 3rd Gen. LNB | 400-500 | 350-400 | 150-200 | 150-200
Operating Characteristics | [9 empty] | Operating Characteristics - Reference Boxes
Biomass Co-Firing |  |  | Capacity Factor (full load hours) |  |  |  | Utility costs |  |  | Capacity Factor Classification
Yes/No | N | Y/N | Input (either % or h/a) | 100 | % |  | Ammonia | 450 | €/t | Baseload I | > 7,000 h/a
Biomass share | 0 | % w/w |  |  | of 8760 h/a |  | Urea | 220 | €/t | Baseload II | 5,000 - 7,000 h/a
Coal share | 100 | % w/w | Resulting capacity factor | 100 | % |  | Electricity | 60 | €/MWh | Medium Load | 2,000 - 5,000 h/a
|  |  | For guidance, see Reference Box |  |  |  | Spec. Power requirement of pressure drop | 0.0414 | Wh/mbar*Nm³ | Peak Load | < 2,000 h/a
[7 empty] | Spec. Power requirement of pressure drop | 2.764e-08 | MWh/mbar/Nm³ | Source: Strauß, Kraftwerkstechnik
Boiler and Fuel Characteristics | [9 empty] | Boiler and Fuel Characteristics - Reference Boxes
Boiler Characteristics | [9 empty] | Reference Box Excess Air (λ)
Excess Air Ratio [λ] | 1.2 | see Reference Box Excess Air | [7 empty] | Oil | 1.03-1.15
Carbon in Ash [xcia] | 2 | % w/w in ash | [7 empty] | Gas | 1.05-1.10
Ash-retained-in-Boiler | 5 | % of total ash | [7 empty] | Coal
S-retained-in-Boiler | 0 | % of total sulphur | [7 empty] | dry bottom | 1.2-1.3
[10 empty] | wet bottom | 1.15-1.25
Please indicate, whether you want to use broad or detailed fuel input data | [9 empty] | grate | 1.3-1.4
Coal | D | d (detailed) / b (broad)
Biomass (if co-firing) | B | d (detailed) / b (broad)
Broad Fuel Composition
Broad Coal Composition |  |  |  | Broad Biomass Composition
Lower Heating Value [LHVfuel] | 29.3 | MJ/kg |  | Lower Heating Value [LHVfuel] | 10 | MJ/kg LHV
Sulphur mass fraction [xS] | 1 | % Sulphur w/w waf |  | Sulphur mass fraction [xS] | 0.1 | % Sulphur w/w waf
Ash mass fraction [xash] | 14.49 | % Ash |  | Ash mass fraction [xash] | 2 | % Ash
Moisture mass fraction [xmoist] | 7.71 | % Moisture |  | Moisture mass fraction [xmoist] | 25 | % Moisture
Spec. stoich. wet flue gas volume [vflue gasstoich,wet] | 7.9512 | Nm³ Flue Gas, stoich, wet/kg Coal |  | Spec. stoich. wet flue gas volume [vflue gasstoich,wet] | 3.1373 | Nm³ Flue Gas, stoich, wet/kg Biomass
Spec. excess air volume [vairstoich,dry] | 1.6389 | Nm³ Excess Air/kg Coal |  | Spec. excess air volume [vairstoich,dry] | 0.6215 | Nm³ Excess Air/kg Biomass
Spec. moisture volume [vmoisture] | 0.53758 | Nm³ moisture/kg Coal |  | Spec. moisture volume [vmoisture] | 0.75288 | Nm³ moisture/kg Biomass
Spec. dry flue gas volume [vflue gasλ,dry] | 9.0525 | Nm³ Flue Gas, λ, dry/kg Coal |  | Spec. dry flue gas volume [vflue gasλ,dry] | 3.0059 | Nm³ Flue Gas, λ, dry/kg Biomass
Oxygen concentration [cO2,act] | 3.802 | % O2, dry |  | Oxygen concentration [cO2,act] | 4.3419 | % O2, dry
Oxygen correction factor [fO2,corr] | 0.87219 | O2 corr. Factor to ref. O2 % |  | Oxygen correction factor [fO2,corr] | 0.90046 | O2 corr. Factor to ref. O2 %
SO2 boiler outlet emissions [loadboSO2,dry,02 act] | 1717.2459 | mg/Nm³, dry, O2 act |  | SO2 boiler outlet emissions [loadboSO2,dry] | 485.2521 | mg/Nm³, dry, O2 act
Dust boiler outlet emissions [loadboash,dry,02 act] | 15516.5578 | mg/Nm³, dry, O2 act |  | Dust boiler outlet emissions [loadboash,dry] | 6449.8355 | mg/Nm³, dry, O2 act
| Detailed Fuel Composition | [8 empty] | Detailed Fuel Composition - Reference Boxes
Detailed Coal Composition | [9 empty] | Origin |  | Composition of exemplary coals (water and ash free, waf) |  |  |  |  | Ash | Moisture |  |  | Logging residue chipsa) | Whole tree chips | Log Chips | Stump Chips | Softwood Bark | Birch Bark | Wood Residue Chips | Saw residue chips | Sawdust | Cutter chips | Grinding dust | Plywood residue | Uncoated wood
| Mass percentages, water and ash free (waf) |  |  |  |  | Ash | Moisture |  |  |  |  | C | H | O | N | S |  |  |  | Moisture content, w-% (fresh chips) | 50-60 | 45-55 | 40-55 | 30-50 | 50-65 | 45-55 | 10 - 50 | 45-60 | 45-60 | 5 - 15 | 5 - 15 | 5 - 15 | 15-30
| C | H | O | N | S |  |  |  |  | Cerrejon | Colombia | 83.4 | 4.95 | 9.47 | 1.37 | 0.81 | 8.41 | 11.83 |  | Net calorific value in dry matter, MJ/kg | 18,5 - 20 | 18,5 - 20 | 18,5 - 20 | 18,5 - 20 | 18,5 - 20 | 21 - 23 | 18,5 - 20 | 18,5 - 20 | 19-19.2 | 19-19.2 | 19-19.2 | 19-19.2 | 18-19
Mass-%, abs. [xi,abs] | 66.1456 | 3.6877 | 5.7027 | 1.7038 | 0.56016 |  |  |  |  | Middelburg | South Africa | 82.44 | 5.02 | 10.43 | 1.38 | 0.73 | 13.55 | 7.42 |  | Net calorific value as received, MJ/kg | 6 - 9 | 6 - 9 | 6 - 10 | 6 - 11 | 6 - 9 | 7 - 11 | 6 - 15 | 41553 | 41553 | 13-16 | 15-17 | 15-17 | 42339
Mass-%, waf. [xi,waf] | 85.02 | 4.74 | 7.33 | 2.19 | 0.72 | 14.49 | 7.71 |  |  | APC | Australia | 88.58 | 4.73 | 4.22 | 1.46 | 1 | 11.12 | 10.27 |  | Bulk densitiy as received (kg/loose m³) | 250-400 | 250-350 | 250-350 | 200-300 | 250-350 | 300-400 | 150-300 | 250-350 | 250-350 | 80-120 | 100-150 | 200-300 | 150-250
Lower Heating Value [LHVfuel] | 22.4435 | MJ/kg | Dust boiler outlet emissions [loadboash,dry] | 18893.6013 | mg/Nm³, dry, O2 act | Spec. moisture volume (Nm³/kg fuel) [vmoisture] | 0.50929 |  |  | Bachatsky | Russia | 87.03 | 4.66 | 5.36 | 2.58 | 0.37 | 9.52 | 10.22 |  | Energy densityMWh/m³ of bulk volume | 0.7-0.9 | 0.7-0.9 | 0.7-0.9 | 0.8-1.0 | 0.5-0.7 | 0.6-0.8 | 0.7-0.9 | 0.5-0.8 | 0.45-0.7 | 0.45-0.55 | 0.5-0.65 | 0.9-1.1 | 0.65-0.8
Spec. dry flue gas volume [vflue gasλ,dry] | 7.4345 | Nm³/kg Coal | SO2 boiler outlet emissions [loadboSO2,dry] | 1505.5124 | mg/Nm³, dry, O2 act | Spec. wet flue gas volume (Nm³/kg coal) [vflue gasλ,wet] | 7.9438 |  |  | Bailey | USA | 84.35 | 5.58 | 6.05 | 2.09 | 1.74 | 7 | 7 |  | Ash content in dry matter, w-% | 1 - 3 | 1 - 2 | 0.5-2 | 1 - 3 | 1 - 3 | 1 - 3 | 0.4-1 | 0.5-2.0 | 0.4-0.5 | 0.4-0.5 | 0.4-0.8 | 0.4-0.8 | 41395
Mass of carbon in ash [mcia] | 0.29571 | kg/kg fuel | [7 empty] | Blackwater | Australia | 86.48 | 4.93 | 5.71 | 1.95 | 0.93 | 14.16 | 8.79 |  | Hydrogen content in dry matter, w-% | 6 - 6.2 | 5.4 - 6 | 5.4 - 6 | 5.4 - 6 | 5.7-5.9 | 6.2-6.8 | 5.4-6.4 | 5.4-6.4 | 6.2-6.4 | 6.2-6.4 | 6.2-6.4 | 6.2-6.4 | 38144
Biomass Composition Input for Fuel Specification | [9 empty] | Douglas | South Africa | 83.3 | 5.11 | 9.47 | 1.42 | 0.7 | 13.75 | 7.65 |  | sulphur content in dry matter, w-% | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.05 | <0.1
| Mass percentages, water and ash free (waf) |  |  |  |  | Ash | Moisture |  |  | Elandsfontein | South Africa | 88.16 | 4.86 | 4.91 | 1.43 | 0.64 | 12.74 | 9 |  | nitrogen content in dry matter, w-% | 0.3-0.5 | 0.3-0.5 | 0.3-0.5 | 0.3-0.5 | 0.3-0.5 | 0.5-0.8 | 0.1-0.5 | 0.1-0.5 | 0.1-0.5 | 0.1-0.5 | 0.1-0.5 | 0.1-0.5 | 0.1-0.5
| C | H | O | N | S |  |  |  |  | Kleinkopje | South Africa | 85.02 | 4.74 | 7.33 | 2.19 | 0.72 | 14.49 | 7.71
Mass-%, abs | 24.4272 | 2.9136 | 20.2128 | 0.4464 | 0.0048 |  |  |  |  | Kromdraai | South Africa | 81.85 | 5.03 | 10.81 | 1.36 | 0.95 | 13.36 | 7.79
Mass-%, waf. | 50.89 | 6.07 | 42.11 | 0.93 | 0.01 | 2 | 50 |  |  | Wood type |  | Composition of exemplary biomass (water and ash free, waf) |  |  |  |  | Ash | Moisture | Average H-mass fraction abs. in coal
Lower Heating Value [LHVfuel] | 4.4112 | MJ/kg | Dust boiler outlet emissions [loadboash,dry] | 3001.2765 | mg/Nm³, dry, O2 act | Spec. moisture volume (Nm³/kg fuel) [vmoisture] | 0.94914 |  |  |  |  | C | H | O | N | S |  |  | 3.9401
Spec. dry flue gas volume [vflue gasλ,dry] | 6.4598 | Nm³/kg Biomass | SO2 boiler outlet emissions [loadboSO2,dry] | 14.8472 | mg/Nm³, dry, O2 act | Spec. wet flue gas volume (Nm³/kg coal) [vflue gasλ,wet] | 7.409 |  |  | ﻿Hybrid poplar |  | 49.2028 | 5.9409 | 44.3688 | 0.4773 | 0.010155 | 1.53 | Depending on storage
Mass of carbon in ash [mcia] | 0.040816 | kg/kg fuel | [7 empty] | Poplar,DN |  | 50.6891 | 6.364 | 42.7341 | 0.19254 | 0.020268 | 1.32
[10 empty] | Hybrid poplar II |  | 51.6036 | 6.2294 | 41.5296 | 0.61678 | 0.020559 | 2.72
[10 empty] | Hybrid poplar DN34 |  | 56.4861 | 4.881 | 38.3381 | 0.26207 | 0.032758 | 8.42
[10 empty] | p.deltoides, Stoneville 66 |  | 51.1013 | 5.6608 | 43.1042 | 0.082338 | 0.051462 | 2.84
[10 empty] | corn stover |  | 46.8649 | 5.9695 | 46.4999 | 0.65493 | 0.010737 | 6.86
[10 empty] | switchgrass |  | 49.3846 | 5.9468 | 43.8205 | 0.76533 | 0.082739 | 3.31
[10 empty] | wheatstraw |  | 48.913 | 5.6612 | 44.6105 | 0.69067 | 0.12455 | 11.68
[10 empty] | ponderosa pine |  | 49.4031 | 6.0086 | 44.4979 | 0.060187 | 0.030093 | 0.31
[10 empty] | Oak |  | 50.64 | 6.23 | 41.85 | 1.28 | < 0,05 | varying
[10 empty] | Beech |  | 50.89 | 6.07 | 42.11 | 0.93 | < 0,05
[10 empty] | Birch |  | 50.61 | 6.23 | 42.04 | 1.12 | < 0,05
[10 empty] | Pine |  | 51.39 | 6.11 | 41.56 | 0.94 | < 0,05
[10 empty] | Spruce |  | 51.39 | 6.11 | 41.56 | 0.94 | < 0,05
| Coal Fuel Spec. Used: |  | Biomass Fuel Spec. Used |  |  | Co-Firing Fuel Spec. Used
Lower Heating Value [LHVfuel] | 22.4435 | MJ/kg LHV | 10 | MJ/kg LHV |  | Lower Heating Value [LHVfuel] | 22.4435 | MJ/kg LHV
Sulphur mass fraction [xS] | 0.72 | % Sulphur w/w waf | 0.1 | % Sulphur w/w waf |  | Sulphur mass fraction [xS] | 0.72 | % Sulphur w/w
Ash mass fraction [xash] | 14.49 | % Ash | 2 | % Ash |  | Ash mass fraction [xash] | 14.49 | % Ash
Spec. wet flue gas volume [vflue gasλ,wet] | 7.9438 | Nm³ Flue Gas,wet,λ /kg Coal | 3.7588 | Nm³ Flue Gas,wet,λ /kg Biomass |  | Spec. wet flue gas volume [vflue gasλ,wet] | 7.9438 | Nm³ Flue Gas,wet,λ /kg Fuel
Annual wet flue gas volume [vflue gasλ,wet,year] | 13952545236.5953 | Nm³ Flue Gas,wet,λ / year | 14817211500 | Nm³ Flue Gas,wet,λ / year |  | Annual wet flue gas volume [vflue gasλ,wet,year] | 13952545236.5953 | Nm³ Flue Gas,wet,λ / year
Spec. dry flue gas volume [vflue gasλ,dry] | 7.4345 | Nm³ flue gas,dry,λ / kg Coal | 3.0059 | Nm³ flue gas,dry,λ / kg Biomass |  | Spec. dry flue gas volume [vflue gasλ,dry] | 7.4345 | Nm³ flue gas,dry,λ / kg Fuel
Annual dry flue gas volume [vflue gasλ,dry,year] | 13058023445.1561 | Nm³ Flue Gas,dry,λ / year | 11849376628.3599 | Nm³ Flue Gas,dry,λ / year |  | Annual dry flue gas volume [vflue gasλ,dry,year] | 13058023445.1561 | Nm³ Flue Gas,dry,λ / year
Oxygen concentration [cO2,act] | 3.7806 | % O2, dry | 4.3419 | % O2, dry |  | Oxygen concentration [cO2,act] | 3.7806 | % O2, dry
Oxygen correction factor [fO2,corr] | 0.87111 | O2 corr. Factor to ref. O2 | 0.90046 | O2 corr. Factor to ref. O2 |  | Oxygen correction factor [fO2,corr] | 0.87111 | O2 corr. Factor to ref. O2
SO2 boiler outlet emissions [loadboSO2,dry,refO2] | 1311.471 | mg/Nm³ SO2, dry, ref O2 | 436.9519 | mg/Nm³ SO2, dry, ref O2 |  | SO2 boiler outlet emissions [loadboSO2,dry,refO2] | 1311.471 | mg/Nm³ SO2, dry, ref O2
NOx boiler outlet emissions [loadboNOx,dry,refO2] | 600 | mg/Nm³ NOx, dry, ref O2 | 600 | mg/Nm³ NOx, dry, ref O2 |  | NOx boiler outlet emissions [loadboNOx,dry,refO2] | 600 | mg/Nm³ NOx, dry, ref O2
Dust boiler outlet emissions [loadboash,dry,refO2] | 16458.4567 | mg/Nm³ dust, dry, ref O2 | 5807.8432 | mg/Nm³ dust, dry, ref O2 |  | Dust boiler outlet emissions [loadboash,dry,refO2] | 16458.4567 | mg/Nm³ dust, dry, ref O2
Moisture | 7.71 | % moisture | 25 | % moisture |  | Moisture | 7.71 | % moisture
Sulphur mass fraction [x real S] | 0.56016 | % Sulphur w/w real | 0.073 | % Sulphur w/w real |  | Sulphur mass fraction [x real S] | 0.56016 | % Sulphur w/w real
SO2 boiler outlet emissions [loadboSO2] | 0.49871 | kg SO2/GJ | 0.14586 | kg SO2/GJ |  | SO2 boiler outlet emissions [loadboSO2] | 0.49871 | kg SO2/GJ
For Illustration:
| Fuel mass input (full load) | 200.5036 | t/h fuel
| Biomass co-firing share (LHV-based) | 0% | % LHV/LHV
At current co-firing share
Note on G4: Just valid for De Nox and dedust techniques
Note on F31: if you choose one solution, please input 0 in the other solution
Note on D32: less than 20% co-firing rate; Please fill in 0 if no co-firing
Note on J76: Please indicate the fuel moisture content. This depends largely on the way of storage and handling and cannot be given in terms of reference values, as the possible range is very large
Note on I79: Please indicate the ash content. Be aware, that ash content may deviate across a single biomass and that bark contains more ash than wood itself

## Liquid fuels - emission calc.
Basic Assumptions
Colour Guide |  |  | Parameter | Value | Unit | Parameter | Value | Unit
Results |  |  | Ref. O2 content [O2,ref.] | 3 | %-Vol. | Depreciation time | 15 | years
Input Data |  |  | Fixed O&M Costs | 2% | of total Investment | Interest rate | 4% | % p. a.
[6 empty] | Capital Recovery Factor | 8.994% | % p. a.
Chemical Data | [8 empty] | Chemical Data - Reference Boxes
Molar masses Mi [kg/kmol]
Elements |  | Substances |  |  | Factors
S | 32.06 | SO2 | 64.06 |  | Mass density of air [δair] | 1.2 | kg/Nm³
N | 14 | NOx (as NO2) | 44 |  | Spec. Ideal gas volume | 22.414 | Nm³/kmol
C | 12 | CO2 | 44
O | 16 | NH3 | 17
Ca | 40 | Urea | 60
H | 1 | CaSO4 x 2 H2O | 172.06
|  | CaCO3 | 100
|  | H2O | 18
Plant Characteristics | [8 empty] | Plant Characteristics - Reference Boxes
Thermal Capacity [bsth] | 1250 | MWth | [6 empty] | NOx Boiler outlet emissions according to technology [mg/Nm³]
Gross Electric Efficiency [ηgross] | 40 | % (LHV) | [6 empty] | Boilers and Process Heaters
Oil fired units
Please enter the appropriate NOx boiler outlet emission concentration
NOx boiler outlet emissions [loadboNOx,dry,O2ref] | 500 | mg/Nm³ NOx, dry, ref O2-% | [6 empty] | uncontrolled | 800 - 1000
For guidance, see Reference Box | [8 empty] | single primary measures | 400 - 500
[9 empty] | multiple primary measures | < 400
Operating Characteristics | [8 empty] | Operating Characteristics - Reference Boxes
Capacity Factor (full load hours) |  |  |  | Utility costs |  |  |  |  | Capacity Factor Classification
Input (either % or h/a) | 100 | % |  | Ammonia | 450 | €/t |  |  | Baseload I | > 7,000 h/a
|  | of 8760 h/a |  | Urea | 220 | €/t |  |  | Baseload II | 5,000 - 7,000 h/a
Resulting capacity factor | 100 | % |  | Electricity | 60 | €/MWh |  |  | Medium Load | 2,000 - 5,000 h/a
For guidance, see Reference Box |  |  |  | Spec. Power requirement of pressure drop | 0.0414 | Wh/mbar*Nm³ |  |  | Peak Load | < 2,000 h/a
|  |  |  | Spec. Power requirement of pressure drop | 2.764e-08 | MWh/mbar/Nm³ |  |  | Source: Strauß, Kraftwerkstechnik
Boiler and Fuel Characteristics | [8 empty] | Boiler and Fuel Characteristics - Reference Boxes
Boiler Characteristics | [8 empty] | Reference Box Excess Air (λ)
Excess Air Ratio [λ] | 1.2 | see Reference Box Excess Air | [6 empty] | Oil | 1.03-1.15
Carbon in Ash [xcia] | 2 | % w/w in ash | [6 empty] | Gas | 1.05-1.10
Ash-retained-in-Boiler | 1 | % of total ash | [6 empty] | Coal
S-retained-in-Boiler | 0 | % of total sulphur | [6 empty] | dry bottom | 1.2-1.3
[9 empty] | wet bottom | 1.15-1.25
Please indicate, whether you want to use broad or detailed fuel input data | [8 empty] | grate | 1.3-1.4
Liquid Fuel | b | d (detailed) / b (broad)
Broad Fuel Composition
Broad Liquid Fuel Composition |  |  |  | Empirical correlation to calculate LHV [Source: Strauß]
Lower Heating Value [LHVfuel] | 42.44 | MJ/kg |  | Density [kg/l at 15°C] | 1.2
Sulphur mass fraction [xS] | 1 | % Sulphur w/w waf |  | S-content [%-w/w] | 1
Ash mass fraction [xash] | 0.1 | % Ash |  | LHV [MJ/kg] | 38.314
Moisture mass fraction [xmoist] | 0.5 | % Moisture
Spec. stoich. dry flue gas volume [vflue gasstoich,dry] | 10.668 | Nm³ Flue Gas, stoich, dry/kg fuel
Spec. excess air volume [vairstoich,dry] | 2.3603 | Nm³ Excess Air/kg fuel
Spec. moisture volume [vmoisture] | 1.1269 | Nm³ moisture/kg fuel
Spec. wet flue gas volume [vflue gasλ,wet] | 14.1552 | Nm³ Flue Gas, λ, wet/kg fuel
Oxygen concentration [cO2,act,dry] | 3.8045 | % O2, dry
Oxygen correction factor [fO2,corr] | 1.0468 | O2 corr. Factor to ref. O2 %
SO2 boiler outlet emissions [loadboSO2,dry] | 1524.4845 | mg/Nm³, dry, O2 act
Dust boiler outlet emissions [loadboash,dry] | 77.5394 | mg/Nm³, dry, O2 act
| Detailed Fuel Composition | [7 empty] | Detailed Fuel Composition - Reference Boxes
Detailed Liquid Fuel Composition | [8 empty] | Type |  | Composition of exemplary liquid fuels (mass-%)
| Mass percentages, water and ash free (waf) |  |  |  |  | Ash | Moisture | HHV |  |  | C | H | O | N | S1 | Moisture | Ash/Metals/Minerals | HHV [kJ/kg]
| C | H | O | N | S |  |  |  | Crude Oil |  | 83-87 | 10-14 | 0,05-1,5 | 0,1-2 | 0,05-6 | <1 | <0,1 | n/a | Hyne, N. J.: Nontechnical Guide to Petroleum Geology, Exploration, Drillind, and Production, PennWell, 2001, pp. 1-4.
Mass-%, abs. [xi,abs] | 87.0744 | 9.94 | 0.994 | 0.3976 | 0.994 | 0.1 | 0.5 | 45 | Gasoline | EU Standard | 87 | 13 | n/a | n/a | n/a | n/a | n/a | 45.7 | Martinez, I.: Fuel properties, available at http://webserver.dmt.upm.es/~isidoro/bk3/c15/Fuel%20properties.pdf
Mass-%, waf. [xi,waf] | 87.6 | 10 | 1 | 0.4 | 1 |  |  |  | Diesel | EU Standard | 84-86 | 13-15 | n/a | n/a | <0,02 | n/a | n/a | 47
Lower Heating Value [LHVfuel] | 42.435 | MJ/kg | Dust boiler outlet emissions [loadboash,dry] | 93.4946 | mg/Nm³, dry, O2 act | Spec. moisture volume (Nm³/kg fuel) [vmoisture] | 1.1202 |  | Biodiesel |  | 77 | 12 | 11 | n/a | 0.01 | n/a | n/a | 40
Spec. dry flue gas volume [vflue gasλ,dry] | 10.8049 | Nm³/kg fuel | SO2 boiler outlet emissions [loadboSO2,dry] | 1838.1762 | mg/Nm³, dry, O2 act | Spec. wet flue gas volume (Nm³/kg fuel [vflue gasλ,wet] | 11.9251 |  | Heavy Fuel Oil |  | 86-88 | 8-10 | n/a | n/a | 1-5 | 0.5 | 0.1 | 43
1 Classification of refined oils acc. To sulphur content
[9 empty] | Low sulphur oil | <0,5%
[9 empty] | Medium sulphur oil | 0,5-2%
[9 empty] | High sulphur oil | >2%
Fuel Spec. Used
Lower Heating Value [LHVfuel] | 42.44 | MJ/kg LHV
Sulphur mass fraction [xS] | 1 | % Sulphur w/w waf
Ash mass fraction [xash] | 0.1 | % Ash
Spec. dry flue gas volume [vflue gasλ,dry] | 13.0283 | Nm³ Flue Gas,dry,λ /kg Fuel
Annual dry flue gas volume [vflue gasλ,dry,year] | 12101188877.4741 | Nm³ Flue Gas,dry,λ / year
Spec. wet flue gas volume [vflue gasλ,wet] | 14.1552 | Nm³ flue gas,wet,λ / kg Fuel
Annual wet flue gas volume [vflue gasλ,wet,year] | 13147923733.7418 | Nm³ Flue Gas,wet,λ / year
Oxygen concentration [cO2,act] | 3.8045 | % O2, dry
Oxygen correction factor [fO2,corr] | 1.0468 | O2 corr. Factor to ref. O2
SO2 boiler outlet emissions [loadboSO2,dry,refO2] | 1595.8057 | mg/Nm³ SO2, dry, ref O2
NOx boiler outlet emissions [loadboNOx,dry,refO2] | 500 | mg/Nm³ NOx, dry, ref O2
Dust boiler outlet emissions [loadboash,dry,refO2] | 81.167 | mg/Nm³ dust, dry, ref O2
Moisture | 0.5 | %
Sulphur mass fraction [x real S] | 0.994 | % Sulphur w/w
SO2 boiler outlet emissions [loadboSO2] | 0.46799 | kg SO2/GJ

## Natural gas - emission calc.
Basic Assumptions
Colour Guide |  |  | Parameter | Value | Unit | Parameter | Value | Unit
Results |  |  | Ref. O2 content [O2,ref.] | 3 | %-Vol. | Depreciation time | 15 | years
Input Data |  |  | Fixed O&M Costs | 2% | of total Investment | Interest rate | 4% | % p. a.
[6 empty] | Capital Recovery Factor | 8.994% | % p. a.
Chemical Data | [10 empty] | Chemical Data - Reference Boxes
Molar masses Mi [kg/kmol]
Elements |  | Substances |  | Substances |  |  |  | Factors
S | 32.06 | SO2 | 64.06 | CH4 | 16 |  |  | Mass density of air [δair] | 1.2 | kg/Nm³
N | 14 | NOx (as NO2) | 44 | C2H6 | 30 |  |  | Spec. Ideal gas volume | 22.414 | Nm³/kmol
C | 12 | CO2 | 44 | C3H8 | 44
O | 16 | NH3 | 17 | C4H10 | 58
Ca | 40 | Urea | 60
H | 1 | CaSO4 x 2 H2O | 172.06
|  | CaCO3 | 100
|  | H2O | 18
Plant Characteristics | [10 empty] | Plant Characteristics - Reference Boxes
Thermal Capacity [bsth] | 1000 | MWth | [8 empty] | NOx Boiler outlet emissions according to technology [mg/Nm³]
Gross Electric Efficiency [ηgross] | 60 | % (LHV) | [8 empty] | Boilers and Process Heaters
gas fired units
Please enter the appropriate NOx boiler outlet emission concentration
NOx boiler outlet emissions [loadboNOx,dry,O2ref] | 600 | mg/Nm³ NOx, dry, ref O2-% | [8 empty] | uncontrolled | 800 - 1000
For guidance, see Reference Box | [10 empty] | single primary measures | 350 - 500
[11 empty] | multiple primary measures | < 350
Operating Characteristics | [10 empty] | Operating Characteristics - Reference Boxes
Capacity Factor (full load hours) |  |  |  | Utility costs | [6 empty] | Capacity Factor Classification
Input (either % or h/a) | 0 | % |  | Ammonia | 450 | €/t |  |  |  |  | Baseload I | > 7,000 h/a
| 6000 | of 8760 h/a |  | Urea | 220 | €/t |  |  |  |  | Baseload II | 5,000 - 7,000 h/a
Resulting capacity factor | 68.4932 | % |  | Electricity | 30 | €/MWh |  |  |  |  | Medium Load | 2,000 - 5,000 h/a
For guidance, see Reference Box |  |  |  | Spec. Power requirement of pressure drop | 0.0414 | Wh/mbar*Nm³ |  |  |  |  | Peak Load | < 2,000 h/a
|  |  |  | Spec. Power requirement of pressure drop | 2.764e-08 | MWh/mbar/Nm³ |  |  |  |  | Source: Strauß, Kraftwerkstechnik
Boiler and Fuel Characteristics | [10 empty] | Boiler and Fuel Characteristics - Reference Boxes
Boiler Characteristics | [10 empty] | Reference Box Excess Air (λ)
Excess Air Ratio [λ] | 1.07 | see Reference Box Excess Air | [8 empty] | Oil | 1.03-1.15
[11 empty] | Gas | 1.05-1.10
Coal
[11 empty] | dry bottom | 1.2-1.3
[11 empty] | wet bottom | 1.15-1.25
Please indicate, whether you want to use broad or detailed fuel input data | [10 empty] | grate | 1.3-1.4
Natural Gas | d | d (detailed) / b (broad)
Broad Fuel Composition
Broad Gas Composition
Lower Heating Value [LHVfuel] | 40.0224 | MJ/Nm³
Density of Natural Gas [δgas] | 0.84 | kg/Nm³
Spec. stoich. dry flue gas volume [vflue gasstoich,dry] | 11.4865 | Nm³ Flue Gas, stoich, dry/Nm³ gas
Spec. excess air volume [vairstoich,dry] | 0.80014 | Nm³ stoich. combustion air/Nm³ gas
Spec. moisture volume [vmoisture] | 2 | Nm³ moisture/Nm³ fuel (ass.: pure CH4)
Spec. wet flue gas volume [vflue gasλ,wet] | 14.2866 | Nm³ Flue Gas, λ, wet/Nm³ gas
Spec. dry flue gas volume [vflue gasλ,dry] | 12.2866 | Nm³ Flue Gas, λ, dry/Nm³ gas
Oxygen concentration [cO2,act] | 1.3676 | % O2, dry
Oxygen correction factor [fO2,corr] | 0.91685 | O2 corr. Factor to ref. O2 %
| Detailed Fuel Composition | [9 empty] | Detailed Fuel Composition - Reference Boxes
Detailed Gas Composition | [10 empty] | Origin |  | Composition of exemplary (treated) natural gases (vol.-%) Source: Reimert 2012
| CH4 | C2H6 | C3H8 | C4H10 | CO2 | N2 | others | HHV [kJ/Nm³] |  |  |  |  | CH4 | C2H6 | C3H8 | C4H10 | CO2 | N2 | others1 | HHV [kJ/Nm³]
Gas Specification in Vol.-% | 86.08 | 8.02 | 2.66 | 0.86 | 1.61 | 0.52 | 0.25 | 44420 |  |  | Ekofisk | Norway | 86.08 | 8.02 | 2.66 | 0.86 | 1.61 | 0.52 | 0.25 | 44420
Lower Heating Value [LHVfuel] | 40.0224 | MJ/Nm³ | Spec. moisture volume (Nm³/Nm³ fuel) [vmoisture] | 2.1241 | Nm³/Nm³fuel | Oxygen for stoich. Combustion needed | 2.2075 | Nm³ |  |  | Groningen | Netherlands | 81.6 | 2.78 | 0.37 | 0.13 | 1 | 14 | 0.12 | 35170
Spec. dry flue gas volume [vflue gasλ,dry] | 10.2067 | Nm³/Nm³fuel | Spec. wet flue gas volume (Nm³/Nm³ fuel) [vflue gasλ,wet] | 12.3308 | Nm³/Nm³fuel | Combustion Air Demand at excess air ratio | 11.2475 | Nm³/Nm³ fuel |  |  | Al Jubail | Saudi Arabia | 71.1 | 25.6 | 1.5 | 0.2 | 1 | 0.6 | 0 | 48150
[11 empty] | - | Indonesia | 83.19 | 3.36 | 2.65 | 1.43 | 8.35 | 0.34 | 0.68 | 40985
[11 empty] | - | Russia | 95.74 | 1 | 0.07 | 0.02 | 1.3 | 1.8 | 0.07 | 39090
[11 empty] | - | United States | 85.9 | 5.8 | 3.3 | 1.6 | 0.2 | 2.1 | 1.1 | 45430
[11 empty] | LNG | - | 89.7 | 7.7 | 2.6 | 0 | 0 | 0 | 0 | 43800
1 others are mainly higher hydrocarbons and will be treated for the following calculation as C4H10
Fuel Spec. Used
Lower Heating Value [LHVfuel] | 40.0224 | MJ/kg LHV
Spec. wet flue gas volume [vflue gasλ,wet] | 12.3308 | Nm³ Flue Gas,wet,λ /kg Fuel
Annual wet flue gas volume [vflue gasλ,wet,year] | 6654919917.3863 | Nm³ Flue Gas,wet,λ / year
Spec. dry flue gas volume [vflue gasλ,dry] | 10.2067 | Nm³ flue gas,dry,λ / kg Fuel
Annual dry flue gas volume [vflue gasλ,dry,year] | 5508548458.589 | Nm³ Flue Gas,dry,λ / year
Oxygen concentration [cO2,act] | 1.5139 | % O2, dry
Oxygen correction factor [fO2,corr] | 0.92374 | O2 corr. Factor to ref. O2 %
NOx boiler outlet emissions [loadboNOx,dry] | 600 | mg/Nm³ NOx, dry, ref O2-%

## Solid fuels - NOx Analysis
| Details on NOx Pollutant Abatement Techniques | [10 empty] | Details on NOx Pollutant Abatement Techniques - Reference Boxes
Which NOx emission goal (at stack) do you want to achieve?
| NOx ELV (for goal achievement calculation) | 300 | mg/Nm³ NOx, dry, ref O2-%
| equivalent NOx ELV at actual O2-% | 344.3871 | mg/Nm³ NOx, dry, act O2-%
| Current %-Gap to goal | 50%
| NOx Emissions | [10 empty] | Reference Box - SNCR Efficiency |  |  | Reference Box - SCR Efficiency
| Primary Measures | [10 empty] | Maximum Achievable SNCR Reduction Rates |  |  | Typical NOx values post-SCR for the current SCR inlet values
| Do you want to upgrade 1° measures? | Y | Yes/No | [8 empty] | Plant Size | Max. Reduction |  | NOx at SCR inlet | 400 | mg/Nm³ NOx, dry, ref O2-%
| New NOx Boiler Outlet Emission | 400 | mg/Nm³ NOx, dry, ref O2-% | [8 empty] | < 100 MWth | 60% |  | SCR Efficiency | SCR outlet emissions
| Reduction achieved with 1° | 33.33% | [9 empty] | 100 - 300 MWth | 55% |  | 60% | 160 | mg/Nm³ NOx, dry, ref O2-%
| Gap-Closure to emission goal (%) | 66.67% | [9 empty] | 300 - 500 MWth | 47.5% |  | 70% | 120 | mg/Nm³ NOx, dry, ref O2-%
| Reduction required with 2° | 25% | [9 empty] | 500 - 700 MWth | 40% |  | 80% | 80 | mg/Nm³ NOx, dry, ref O2-%
[12 empty] | > 700 MWth | 35% |  | 90% | 40 | mg/Nm³ NOx, dry, ref O2-%
| Secondary Measures | [10 empty] | Sources: | US EPA: Air Pollution Control Cost Manual, 2002
| NOx emissions before 2° measures | 400 | mg/Nm³ NOx, dry, ref O2-% | [9 empty] | EPRI: SNCR Guidelines Update, 2004
| Does literature suggest SNCR? | Y | Yes/No | See "Reference Box - SNCR Efficiency" and "Reference Box - SCR Efficiency" | [8 empty] | Rentz: Emission Control at Stationary Sources in the Federal Republic of Germany, 1996
| New NOx outlet emissions | 300 | mg/Nm³ NOx, dry, ref O2-% | [9 empty] | EGTEI Questionnaires 2012
| Total reduction achieved | 50%
| Degree of Over-Achievement to ELV | 0%
Conclusion of technology choice
| NOx stack emissions with selected technologies | 300 | mg/Nm³ NOx, dry, ref O2-%
| Do you want to install SCR? | Y | Yes/No
| Do you want to install SNCR? | y | Yes/No
| The technology choice is suitable | N | CHECK
| The technology choice fits with the emission goals | OK | CHECK
| Economic Analysis | [10 empty] | Economic Analysis - Reference Boxes
| Primary Measures | [10 empty] | Reference Box - Investment Data (in EUR/kWth 2010)
| NOx emissions saved | 2998.01 | t/a | [9 empty] | LNB | SNCR | SCR
| Spec. Equipment Investment (see Ref. Box) | 30 | €/kWth | See "Reference Box - Investment Data" | [7 empty] | Survey Data (see spreadsheet) | 6.3095 | 15.783 | 48.7997
| Total Investment | 37500000 | € | [8 empty] | Survey Data - lower end | 4.3512 | 11.3714 | 32.1471
| Capital Cost p.a. | 3372791.2639 | €/a | [8 empty] | Survey Data - upper end | 8.2678 | 20.1946 | 55.5714
| Fixed O&M Costs | 750000 | €/a | [8 empty] | Total Investment at | 1250 | MWth (in Mio. EUR)
[12 empty] | Survey Data (see spreadsheet) | 7.8869 | 19.7287 | 60.9996
| Total Costs p. a. | 4122791.2639 | €/a | [8 empty] | Survey Data - lower end | 5.4389 | 14.2142 | 40.1838
| spec. NOx reduction costs | 1375.176 | €/t | [8 empty] | Survey Data - upper end | 10.3348 | 25.2432 | 69.4642
[12 empty] | Old EGTEI function - retrofit | n/a | n/a | 25.1431
[12 empty] | Old EGTEI function - new plant | 4.8462 | n/a | 17.9594
Secondary Measures - SNCR (if SNCR = Y)
| SNCR | y
| NOx emissions saved | 1499.005 | t/a
Capital Costs
| Spec. Equipment Investment | 16 | €/kWth | See "Reference Box - Investment Data"
| Total Investment | 20000000 | €
| Capital Cost p.a. | 1798822.0074 | €/a
| Operating Costs | [10 empty] | Reference Box Utilities - Literature data
| Fixed O&M Costs | 400000 | €/a
| Anhydrous NH3 (Y/N) | y | [9 empty] | Stoiciometric Ratio (Literature)
| Urea (Y/N) | N | [9 empty] | SCR | 0.8-0.9
| Stoichiometric Ratio | 1.75 |  | See "Reference Box - Utilities" and "Reference Box - Utility Calculation" | [7 empty] | SNCR | 1.5-2.0
| reagent consumption | 1013.5318 | t/a | [8 empty] | Pressure Drop for SCR/SNCR
| reagent cost | 456089.3065 | €/a | [8 empty] | Injection & Mixing | 1.5 | mbar
| utility electricity consumption | 0.1 | MWh/h | [8 empty] | Catalyst Layer | 2.5 | mbar
| utility electricity cost | 52560 | €/a | [8 empty] | SCR excl Inj., Mix. & Cat. | 1.5 | mbar
| pressure drop cons. | 0.0621 | MWh/Mio. Nm³
| pressure drop cost | 77980.7753 | €/a | [8 empty] | Catalyst Cost & Design Data for Hard Coal Fired Units
[13 empty] | Min | Max | Unit | No. of References
| Operating Costs p. a. | 986630.0818 | €/a | [8 empty] | Spec. Cat. Requirement | 0.5 | 0.59 | m³/MWth | 2
| Total Costs p. a. | 2785452.0893 | €/a | [8 empty] | Total Cat. Lifetime | 24000 | 36000 | h | 2
| spec. NOx reduction cost | 1858.2007 | €/t | [8 empty] | No. Of cat. Regenerations | 0 | 3 |  | 3
| share capital costs to total costs | 64.58% | [9 empty] | Spec. Cat. Cost | 4000 | 5000 | €/m³ | 2
| share operating costs to total costs | 35.42% | [9 empty] | Spec. Cat. Regeneration Cost | 2500 |  | €/m³ | 1
| Secondary Measures - SCR (if SCR = Y) | [10 empty] | Reference Box - Calculated Utilities
| SCR (Y/N) | Y | Y/N | [8 empty] | Stoiciometric Ratio used in Calculation
| NOx emissions saved | 1499.005 | t/a | [8 empty] | SCR | 0.9 | see above for guidance
| Capital Costs | [10 empty] | SNCR | 1.75
| Spec. Equipment Investment | 40 | €/kWth | See "Reference Box - Investment Data" | [7 empty] | No. Of catalyst layers | 3
| Total Investment | 50000000 | €
| Capital Cost p.a. | 4497055.0185 | €/a | [8 empty] | Total SCR Pressure Drop | 10.5 | mbar
| Operating Costs | [10 empty] | Total SNCR Pressure Drop | 1.5 | mbar
| Fixed O&M Costs | 1000000 | €/a
| Anhydrous NH3 (Y/N) | y
| Urea (Y/N) | N
| Stoichiometric Ratio | 0.9 | [9 empty] | Catalyst Cost Calculation Box (see above for guidance)
| reagent consumption | 521.2449 | t/a | See "Reference Box - Utilities" and "Reference Box - Utility Calculation" | [7 empty] | Spec. Cat. Volume | 0.5 | m³/MWth
| reagent cost | 234560.2148 | €/a | [8 empty] | Total Cat. Volume | 625 | m³
| utility electricity consumption | 0.1 | MWh/h | [8 empty] | Total Cat. Lifetime | 20000 | h
| utility electricity cost | 52560 | €/a | [8 empty] | Lifetime Reduction Biomass Co-firing | 20%
| pressure drop cons. | 0.4347 | MWh/Mio. Nm³ | [8 empty] | Total Cat. Lifetime Biomass | 16000 | h
| pressure drop cost | 3821057.991 | €/a | [8 empty] | No. Of cat. Regenerations | 2
| annualised catalyst costs | 2463750 | €/a | [8 empty] | Cat. Lifetime acc. To operating regime | 2.2831 | a
[12 empty] | Annualised catalyst cost | 2463750 | €/a
| Operating Costs (incl. Catalyst Costs) p. a. | 7571928.2058 | €/a
| Total Costs p. a. | 12068983.2244 | €/a
| spec. NOx reduction cost | 8051.3295 | €/t
| share capital costs to total costs | 37.26%
| share operating costs to total costs | 62.74%
Summary
| spec. NOx emissions saved | 300 | mg/Nm³ NOx, dry, ref O2-%
| spec. NOx emissions saved | 344.3871 | mg/Nm³ NOx, dry, act O2-%
| total NOx emissions saved | 4497.015 | t/a | Share
| thereof 1° measures | 2998.01 | t/a | 66.67%
| thereof 2° measures | 1499.005 | t/a | 33.33%
Investment Data (Background Information) for COAL fired power plant
Conversion: | Conversion with currency exchange rate of author at given date into EUR, time conversion with CEPCI to 2010 afterwards | [12 empty] | CEPCI Factors | Factor | CEPCI Value
| Currency | Exchange Rate | Date | Reporting Country | [9 empty] | 2010 | 1 | 550.8
Nalbandian (IEA): | USD:EUR | 1.2 | 2006 | US | [9 empty] | 2009 | 1.0554 | 521.9
Brandwood (JEP): | EUR:GBP | 1.36 | 2007 | UK | [9 empty] | 2008 | 0.95725 | 575.4
[14 empty] | 2007 | 1.0483 | 525.4
Plant Electric Efficiency | 40% | Conversion kWe -> kWth | [11 empty] | 2006 | 1.1025 | 499.6
[14 empty] | 2005 | 1.1764 | 468.2
[14 empty] | 2004 | 1.24 | 444.2
|  | EUR / kWe |  | EUR / kWth |  |  | Given Literature Values | [6 empty] | 2003 | 1.3712 | 401.7
|  | Min | Max | Min | Max | Orignial Source | Min | Max | Unit | Country | Cost Year | Suppl. Info |  | 2002 | 1.3923 | 395.6
JEP | LNB+SNCR | 28.515 | 28.515 | 11.406 | 11.406 | Barmor, 2006 | 20 | 20 | GBP/kWe | UK | 2007 |  |  | 2001 | 1.3969 | 394.3
IEA | LNB | 2.3528 | 2.3528 | 5.8821 | 5.8821 | Orfanoudakis, 2005 | 5 | 5 | EUR/kWth | Greece | 2005 |  |  | 2000 | 1.3976 | 394.1
IEA | LNB | 5.8333 | 20.8333 | 2.3333 | 8.3333 |  | 7 | 25 | USD/kWe | UK |  | High End: OFA
IEA | LNB | 5.8333 | 30 | 2.3333 | 12 |  | 7 | 36 | USD/kWe | US |  | High End: OFA
IEA | LNB | 17.1397 | 17.1397 | 6.8559 | 6.8559 | Schneck, 2003 | 15 | 15 | USD/kWe | Canada | 2003
JEP | SCR | 114.0598 | 185.3472 | 45.6239 | 74.1389 | Literature Survey | 80 | 130 | GBP/kWe | US | 2007
JEP | SCR | 285.1496 | 299.4071 | 114.0598 | 119.7628 | Literature Survey | 200 | 210 | GBP/kWe | US | 2007 | Complicated
JEP | SCR | 52.4172 | 52.4172 | 20.9669 | 20.9669 | Literature Survey | 50 | 50 | EUR/kWe | France | 2007
JEP | SCR | 85.5449 | 114.0598 | 34.218 | 45.6239 | Barmor, 2006 | 60 | 80 | GBP/kWe | UK | 2007 | low eff. to high eff. SCR
IEA | SCR | 147.0525 | 205.8736 | 58.821 | 82.3494 | Orfanoudakis, 2005 | 50 | 70 | EUR/kWth | Greece | 2005
IEA | SCR | 50.5304 | 128.6229 | 20.2122 | 51.4492 |  | 55 | 140 | USD/kWe | US
IEA | SCR | 41.3431 | 82.6861 | 16.5372 | 33.0745 |  | 45 | 90 | USD/kWe | UK
IEA | SCR | 91.8735 | 91.8735 | 36.7494 | 36.7494 |  | 100 | 100 | USD/kWe | US
IEA | SCR | 79.9851 | 182.823 | 31.994 | 73.1292 | Morris, 2003 | 70 | 160 | USD/kWe | US | 2003 | Average 110 USD/kWe
IEA | SCR | 58.2044 | 128.0497 | 23.2818 | 51.2199 | US EPA, 2002 | 50 | 110 | USD/kWe | US | 2001 | US EPA Cost Methodology
IEA | SCR | 82.6655 | 123.9982 | 33.0662 | 49.5993 | US DOE, 2005 | 80 | 120 | USD/kWe | US | 2004
IEA | SNCR | 7.0585 | 14.117 | 17.6463 | 35.2926 | Orfanoudakis, 2005 | 15 | 30 | EUR/kWth | Greece | 2005
JEP | SNCR | 2.0386 | 2.0386 | 5.0965 | 5.0965 | SNCR recalculated by subtracting the LNB average from LNB+SNCR Investment of Barmor, 2006
|  |  |  | Lower | Upper
Total Average LNB | 6.3095 | EUR/kWth | EUR 2010 | 4.3512 | 8.2678
Total Average SCR | 48.7997 | EUR/kWth | EUR 2010 | 32.1471 | 55.5714
Total Average SNCR | 15.783 | EUR/kWth | EUR 2010 | 11.3714 | 20.1946
Old EGTEI Cost Function
| Constant | Linear Factor | Retrofit Factor | Year Factor 2000 -> 2010
| [1000 EUR] | [EUR/kWth] | % | Ratio
LNB | 780 | 2.15 | 0 | 1.3976
SCR | 5000 | 6.28 | 40% | 1.3976
Note on D12: Choose the "new" boiler outlet emission according to your preferred technology. For guiding, see Reference Box "NOx Boiler Outlet Emissions According to Plant Technology".
Note on D14: Gap closure between old boiler outlet emissions (spreadsheet emission calculation, cell D92) and new (retrofitted) boiler outlet emissions (cell D12) with respect to the corresponding ELV (cell D5).
Note on D28: (Y) if you select ONE out of the two 2° abatement technologies, (N) if you select both. Please only select SCR or SNCR.

## Liquid fuels - NOx Analysis
| Details on NOx Pollutant Abatement Techniques | [10 empty] | Details on NOx Pollutant Abatement Techniques - Reference Boxes
Which NOx emission goal (at stack) do you want to achieve?
| NOx ELV (for goal achievement calculation) | 300 | mg/Nm³ NOx, dry, ref O2-%
| equivalent NOx ELV at actual O2-% | 286.5921 | mg/Nm³ NOx, dry, act O2-%
| Current %-Gap to goal | 40%
| NOx Emissions | [10 empty] | Reference Box - SNCR Efficiency |  |  | Reference Box - SCR Efficiency
| Primary Measures | [10 empty] | Maximum Achievable SNCR Reduction Rates |  |  | Typical NOx values post-SCR for the current SCR inlet values
| Do you want to upgrade 1° measures? | y | Yes/No | [11 empty] | NOx at SCR inlet | 400 | mg/Nm³ NOx, dry, ref O2-%
| New NOx Boiler Outlet Emission | 400 | mg/Nm³ NOx, dry, ref O2-% | [8 empty] | unknown. See spreadsheet "Solid Fuels NOx analysis" for orientation |  |  | SCR Efficiency | SCR outlet emissions
| Reduction achieved with 1° | 20% | [12 empty] | 60% | 160 | mg/Nm³ NOx, dry, ref O2-%
| Gap-Closure to emission goal (%) | 50% | [12 empty] | 70% | 120 | mg/Nm³ NOx, dry, ref O2-%
| Reduction required with 2° | 25% | [12 empty] | 80% | 80 | mg/Nm³ NOx, dry, ref O2-%
[15 empty] | 90% | 40 | mg/Nm³ NOx, dry, ref O2-%
Secondary Measures
| NOx emissions before 2° measures | 400 | mg/Nm³ NOx, dry, ref O2-%
| New NOx outlet emissions | 150 | mg/Nm³ NOx, dry, ref O2-%
| Total reduction achieved | 70%
| Degree of Over-Achievement to ELV | 50%
Conclusion of technology choice
| NOx stack emissions with selected technologies | 400 | mg/Nm³ NOx, dry, ref O2-%
| Do you want to install SCR? | n | Yes/No
| Do you want to install SNCR? | n | Yes/No
| The technology choice is suitable | Y | CHECK
| The technology choice fits with the emission goals | OK | CHECK
| Economic Analysis | [10 empty] | Economic Analysis - Reference Boxes
Primary Measures
| NOx emissions saved | 1156.0352 | t/a
| Spec. Equipment Investment (see Ref. Box) | 20 | €/kWth | See "Reference Box - Investment Data"
| Total Investment | 25000000 | €
| Capital Cost p.a. | 2248527.5093 | €/a
| Fixed O&M Costs | 500000 | €/a
| Total Costs p. a. | 2748527.5093 | €/a
| spec. NOx reduction costs | 2377.5466 | €/t
Secondary Measures - SNCR (if SNCR = Y)
| SNCR | n
| NOx emissions saved | n/a | t/a
Capital Costs
| Spec. Equipment Investment | 25 | €/kWth | See "Reference Box - Investment Data"
| Total Investment | 0 | €
| Capital Cost p.a. | 0 | €/a
| Operating Costs | [10 empty] | Reference Box Utilities - Literature data
| Fixed O&M Costs | 0 | €/a
| NH3 (Y/N) | n | [9 empty] | Stoichiometric Ratio (Literature)
| Urea (Y/N) | Y | [9 empty] | SCR | 0.8-0.9
| SR | 1.75 |  | See "Reference Box - Utilities" and "Reference Box - Utility Calculation" | [7 empty] | SNCR | 1.5-2.5
| reagent consumption | 0 | t/a | [8 empty] | Pressure Drop for SCR/SNCR
| reagent cost | 0 | €/a | [8 empty] | Injection & Mixing | 1.5 | mbar
| utility electricity consumption | 0.01 | MWh/h | [8 empty] | Catalyst Layer | 2.5 | mbar
| utility electricity cost | 0 | €/a | [8 empty] | SCR excl Inj., Mix. & Cat. | 1.5 | mbar
| pressure drop cons. | 0.0621 | MWh/Mio. Nm³
| pressure drop cost | 0 | €/a | [8 empty] | Catalyst Cost & Design Data for Hard Coal Fired Units
[13 empty] | Min | Max | Unit | No. of References
| Operating Costs p. a. | 0 | €/a | [8 empty] | Spec. Cat. Requirement | 0.11 |  | m³/MWth | 1
| Total Costs p. a. | 0 | €/a | [8 empty] | Total Cat. Lifetime | 40000 | 80000 | h | 3
| spec. NOx reduction cost | n/a | €/t | [8 empty] | No. Of cat. Regenerations | 0 | 4 |  | 4
| share capital costs to total costs | n/a | [9 empty] | Spec. Cat. Cost | 4000 | 15000 | €/m³ | 2
| share operating costs to total costs | n/a | [9 empty] | Spec. Cat. Regeneration Cost | < 50% of costs for new catalyst
| Secondary Measures - SCR (if SCR = Y) | [10 empty] | Reference Box - Calculated Utilities
| SCR (Y/N) | n | Y/N | [8 empty] | Stoiciometric Ratio used in Calculation
| NOx emissions saved | 0 | t/a | [8 empty] | SCR | 0.9 | see above for guidance
| Capital Costs | [10 empty] | SNCR | 1.75
| Spec. Equipment Investment | 40 | €/kWth | See "Reference Box - Investment Data" | [7 empty] | No. Of catalyst layers | 3
| Total Investment | 0 | €
| Capital Cost p.a. | 0 | €/a | [8 empty] | Total SCR Pressure Drop | 10.5 | mbar
| Operating Costs | [10 empty] | Total SNCR Pressure Drop | 1.5 | mbar
| Fixed O&M Costs | 0 | €/a
| NH3 (Y/N) | y
| Urea (Y/N) | N
| Stoichiometric Ratio | 0.9 | [9 empty] | Catalyst Cost Calculation Box (see above for guidance)
| reagent consumption | 0 | t/a | See "Reference Box - Utilities" and "Reference Box - Utility Calculation" | [7 empty] | Spec. Cat. Volume | 0.5 | m³/MWth
| reagent cost | 0 | €/a | [8 empty] | Total Cat. Volume | 625 | m³
| utility electricity consumption | 0.01 | MWh/h | [8 empty] | Total Cat. Lifetime | 20000 | h
| utility electricity cost | 0 | €/a | [8 empty] | Lifetime Reduction Biomass Co-firing | 20%
| pressure drop cons. | 0.4347 | MWh/Mio. Nm³ | [8 empty] | Total Cat. Lifetime Biomass | 16000 | h
| pressure drop cost | 0 | €/a | [8 empty] | No. Of cat. Regenerations | 2
| annualised catalyst costs | 0 | €/a | [8 empty] | Cat. Lifetime acc. To operating regime | 1.8265 | a
[12 empty] | Annualised catalyst cost | 1369434.375 | €/a
| Operating Costs (incl. Catalyst Costs) p. a. | 0 | €/a
| Total Costs p. a. | 0 | €/a
| spec. NOx reduction cost | n/a | €/t
| share capital costs to total costs | n/a
| share operating costs to total costs | n/a
Summary
| spec. NOx emissions saved | 350 | mg/Nm³ NOx, dry, ref O2-%
| spec. NOx emissions saved | 334.3575 | mg/Nm³ NOx, dry, act O2-%
| total NOx emissions saved | 4046.123 | t/a | Share
| thereof 1° measures | 1156.0352 | t/a | 28.57%
| thereof 2° measures | 2890.0879 | t/a | 71.43%
Investment Data (Background Information) for COAL fired power plant
Conversion: | Conversion with currency exchange rate of author at given date into EUR, time conversion with CEPCI to 2010 afterwards | [12 empty] | CEPCI Factors | Factor | CEPCI Value
| Currency | Exchange Rate | Date | Reporting Country | [9 empty] | 2010 | 1 | 550.8
Nalbandian (IEA): | USD:EUR | 1.2 | 2006 | US | [9 empty] | 2009 | 1.0554 | 521.9
Brandwood (JEP): | EUR:GBP | 1.36 | 2007 | UK | [9 empty] | 2008 | 0.95725 | 575.4
[14 empty] | 2007 | 1.0483 | 525.4
Plant Electric Efficiency | 40% | Conversion kWe -> kWth | [11 empty] | 2006 | 1.1025 | 499.6
[14 empty] | 2005 | 1.1764 | 468.2
[14 empty] | 2004 | 1.24 | 444.2
|  | EUR / kWe |  | EUR / kWth |  |  | Given Literature Values | [6 empty] | 2003 | 1.3712 | 401.7
|  | Min | Max | Min | Max | Orignial Source | Min | Max | Unit | Country | Cost Year | Suppl. Info |  | 2002 | 1.3923 | 395.6
JEP | LNB+SNCR | 28.515 | 28.515 | 11.406 | 11.406 | Barmor, 2006 | 20 | 20 | GBP/kWe | UK | 2007 |  |  | 2001 | 1.3969 | 394.3
IEA | LNB | 2.3528 | 2.3528 | 5.8821 | 5.8821 | Orfanoudakis, 2005 | 5 | 5 | EUR/kWth | Greece | 2005 |  |  | 2000 | 1.3976 | 394.1
IEA | LNB | 5.8333 | 20.8333 | 2.3333 | 8.3333 |  | 7 | 25 | USD/kWe | UK |  | High End: OFA
IEA | LNB | 5.8333 | 30 | 2.3333 | 12 |  | 7 | 36 | USD/kWe | US |  | High End: OFA
IEA | LNB | 17.1397 | 17.1397 | 6.8559 | 6.8559 | Schneck, 2003 | 15 | 15 | USD/kWe | Canada | 2003
JEP | SCR | 114.0598 | 185.3472 | 45.6239 | 74.1389 | Literature Survey | 80 | 130 | GBP/kWe | US | 2007
JEP | SCR | 285.1496 | 299.4071 | 114.0598 | 119.7628 | Literature Survey | 200 | 210 | GBP/kWe | US | 2007 | Complicated
JEP | SCR | 52.4172 | 52.4172 | 20.9669 | 20.9669 | Literature Survey | 50 | 50 | EUR/kWe | France | 2007
JEP | SCR | 85.5449 | 114.0598 | 34.218 | 45.6239 | Barmor, 2006 | 60 | 80 | GBP/kWe | UK | 2007 | low eff. to high eff. SCR
IEA | SCR | 147.0525 | 205.8736 | 58.821 | 82.3494 | Orfanoudakis, 2005 | 50 | 70 | EUR/kWth | Greece | 2005
IEA | SCR | 50.5304 | 128.6229 | 20.2122 | 51.4492 |  | 55 | 140 | USD/kWe | US
IEA | SCR | 41.3431 | 82.6861 | 16.5372 | 33.0745 |  | 45 | 90 | USD/kWe | UK
IEA | SCR | 91.8735 | 91.8735 | 36.7494 | 36.7494 |  | 100 | 100 | USD/kWe | US
IEA | SCR | 79.9851 | 182.823 | 31.994 | 73.1292 | Morris, 2003 | 70 | 160 | USD/kWe | US | 2003 | Average 110 USD/kWe
IEA | SCR | 58.2044 | 128.0497 | 23.2818 | 51.2199 | US EPA, 2002 | 50 | 110 | USD/kWe | US | 2001 | US EPA Cost Methodology
IEA | SCR | 82.6655 | 123.9982 | 33.0662 | 49.5993 | US DOE, 2005 | 80 | 120 | USD/kWe | US | 2004
IEA | SNCR | 7.0585 | 14.117 | 17.6463 | 35.2926 | Orfanoudakis, 2005 | 15 | 30 | EUR/kWth | Greece | 2005
JEP | SNCR | 2.0386 | 2.0386 | 5.0965 | 5.0965 | SNCR recalculated by subtracting the LNB average from LNB+SNCR Investment of Barmor, 2006
|  |  |  | Lower | Upper
Total Average LNB | 6.3095 | EUR/kWth | EUR 2010 | 4.3512 | 8.2678
Total Average SCR | 48.7997 | EUR/kWth | EUR 2010 | 32.1471 | 55.5714
Total Average SNCR | 15.783 | EUR/kWth | EUR 2010 | 11.3714 | 20.1946
Old EGTEI Cost Function
| Constant | Linear Factor | Retrofit Factor | Year Factor 2000 -> 2010
| [1000 EUR] | [EUR/kWth] | % | Ratio
LNB | 780 | 2.15 | 0 | 1.3976
SCR | 5000 | 6.28 | 40% | 1.3976
Note on D12: Choose the "new" boiler outlet emission according to your preferred technology. For guiding, see Reference Box "NOx Boiler Outlet Emissions According to Plant Technology".
Note on D14: Gap closure between old boiler outlet emissions (spreadsheet emission calculation, cell D92) and new (retrofitted) boiler outlet emissions (cell D12) with respect to the corresponding ELV (cell D5).
Note on D28: (Y) if you select ONE out of the two 2° abatement technologies, (N) if you select both. Please only select SCR or SNCR.

## Natural gas - NOx Analysis
| Details on NOx Pollutant Abatement Techniques | [10 empty] | Details on NOx Pollutant Abatement Techniques - Reference Boxes
Which NOx emission goal (at stack) do you want to achieve?
| NOx ELV (for goal achievement calculation) | 200 | mg/Nm³ NOx, dry, ref O2-%
| equivalent NOx ELV at actual O2-% | 216.512 | mg/Nm³ NOx, dry, act O2-%
| Current %-Gap to goal | 66.67%
| NOx Emissions | [10 empty] | Reference Box - SNCR Efficiency |  |  | Reference Box - SCR Efficiency
| Primary Measures | [10 empty] | Maximum Achievable SNCR Reduction Rates |  |  | Typical NOx values post-SCR for the current SCR inlet values
| Do you want to upgrade 1° measures? | n | Yes/No | [11 empty] | NOx at SCR inlet | 600 | mg/Nm³ NOx, dry, ref O2-%
| New NOx Boiler Outlet Emission | 400 | mg/Nm³ NOx, dry, ref O2-% | [8 empty] | unknown. See spreadsheet "Solid Fuels NOx analysis" for orientation |  |  | SCR Efficiency | SCR outlet emissions
| Reduction achieved with 1° | n/a | [12 empty] | 60% | 240 | mg/Nm³ NOx, dry, ref O2-%
| Gap-Closure to emission goal (%) | n/a | [12 empty] | 70% | 180 | mg/Nm³ NOx, dry, ref O2-%
| Reduction required with 2° | 66.67% | [12 empty] | 80% | 120 | mg/Nm³ NOx, dry, ref O2-%
[15 empty] | 90% | 60 | mg/Nm³ NOx, dry, ref O2-%
Secondary Measures
| NOx emissions before 2° measures | 600 | mg/Nm³ NOx, dry, ref O2-%
| New NOx outlet emissions | 150 | mg/Nm³ NOx, dry, ref O2-%
| Total reduction achieved | 75%
| Degree of Over-Achievement to ELV | 25%
Conclusion of technology choice
| NOx stack emissions with selected technologies | 150 | mg/Nm³ NOx, dry, ref O2-%
| Do you want to install SCR? | Y | Yes/No
| Do you want to install SNCR? | N | Yes/No
| The technology choice is suitable | Y | CHECK
| The technology choice fits with the emission goals | OK | CHECK
| Economic Analysis | [10 empty] | Economic Analysis - Reference Boxes
Primary Measures
| NOx emissions saved | 0 | t/a
| Spec. Equipment Investment (see Ref. Box) | 20 | €/kWth | See "Reference Box - Investment Data"
| Total Investment | n/a | €
| Capital Cost p.a. | n/a | €/a
| Fixed O&M Costs | n/a | €/a
| Total Costs p. a. | n/a | €/a
| spec. NOx reduction costs | n/a | €/t
Secondary Measures - SNCR (if SNCR = Y)
| SNCR | N
| NOx emissions saved | n/a | t/a
Capital Costs
| Spec. Equipment Investment | 2000 | €/kWth | See "Reference Box - Investment Data"
| Total Investment | 0 | €
| Capital Cost p.a. | 0 | €/a
| Operating Costs | [10 empty] | Reference Box Utilities - Literature data
| Fixed O&M Costs | 0 | €/a
| NH3 (Y/N) | n | [9 empty] | Stoichiometric Ratio (Literature)
| Urea (Y/N) | Y | [9 empty] | SCR | 0.8-0.9
| SR | 1.75 |  | See "Reference Box - Utilities" and "Reference Box - Utility Calculation" | [7 empty] | SNCR | 1.5-2.5
| reagent consumption | 0 | t/a | [8 empty] | Pressure Drop for SCR/SNCR
| reagent cost | 0 | €/a | [8 empty] | Injection & Mixing | 1.5 | mbar
| utility electricity consumption | 0.01 | MWh/h | [8 empty] | Catalyst Layer | 2.5 | mbar
| utility electricity cost | 0 | €/a | [8 empty] | SCR excl Inj., Mix. & Cat. | 1.5 | mbar
| pressure drop cons. | 0.0621 | MWh/Mio. Nm³
| pressure drop cost | 0 | €/a | [8 empty] | Catalyst Cost & Design Data for Hard Coal Fired Units
[13 empty] | Min | Max | Unit | No. of References
| Operating Costs p. a. | 0 | €/a | [8 empty] | Spec. Cat. Requirement | 0.11 |  | m³/MWth | 1
| Total Costs p. a. | 0 | €/a | [8 empty] | Total Cat. Lifetime | 40000 | 80000 | h | 3
| spec. NOx reduction cost | n/a | €/t | [8 empty] | No. Of cat. Regenerations | 0 | 4 |  | 4
| share capital costs to total costs | n/a | [9 empty] | Spec. Cat. Cost | 4000 | 15000 | €/m³ | 2
| share operating costs to total costs | n/a | [9 empty] | Spec. Cat. Regeneration Cost | < 50% of costs for new catalyst
| Secondary Measures - SCR (if SCR = Y) | [10 empty] | Reference Box - Calculated Utilities
| SCR (Y/N) | Y | Y/N | [8 empty] | Stoichiometric Ratio used in Calculation
| NOx emissions saved | 2683.5008 | t/a | [8 empty] | SCR | 0.9 | see above for guidance
| Capital Costs | [10 empty] | SNCR | 1.75
| Spec. Equipment Investment | 80 | €/kWth | See "Reference Box - Investment Data" | [7 empty] | No. Of catalyst layers | 3
| Total Investment | 80000000 | €
| Capital Cost p.a. | 7195288.0297 | €/a | [8 empty] | Total SCR Pressure Drop | 10.5 | mbar
| Operating Costs | [10 empty] | Total SNCR Pressure Drop | 1.5 | mbar
| Fixed O&M Costs | 1600000 | €/a
| NH3 (Y/N) | y
| Urea (Y/N) | N
| Stoichiometric Ratio | 0.9 | [9 empty] | Catalyst Cost Calculation Box (see above for guidance)
| reagent consumption | 933.1264 | t/a | See "Reference Box - Utilities" and "Reference Box - Utility Calculation" | [7 empty] | Spec. Cat. Volume | 0.11 | m³/MWth
| reagent cost | 419906.8823 | €/a | [8 empty] | Total Cat. Volume | 110 | m³
| utility electricity consumption | 0.01 | MWh/h | [8 empty] | Total Cat. Lifetime | 20000 | h
| utility electricity cost | 1800 | €/a | [8 empty] | Lifetime Reduction Biomass Co-firing | 20%
| pressure drop cons. | 0.4347 | MWh/Mio. Nm³ | [8 empty] | Total Cat. Lifetime Biomass | 16000 | h
| pressure drop cost | 86786.8106 | €/a | [8 empty] | No. Of cat. Regenerations | 2
| annualised catalyst costs | 165082.5 | €/a | [8 empty] | Cat. Lifetime acc. To operating regime | 2.6667 | a
[12 empty] | Annualised catalyst cost | 165082.5 | €/a
| Operating Costs (incl. Catalyst Costs) p. a. | 2273576.1929 | €/a
| Total Costs p. a. | 9468864.2226 | €/a
| spec. NOx reduction cost | 3528.5491 | €/t
| share capital costs to total costs | 75.99%
| share operating costs to total costs | 24.01%
Summary
| spec. NOx emissions saved | 450 | mg/Nm³ NOx, dry, ref O2-%
| spec. NOx emissions saved | 487.1521 | mg/Nm³ NOx, dry, act O2-%
| total NOx emissions saved | 2683.5008 | t/a | Share
| thereof 1° measures | 0 | t/a | 0%
| thereof 2° measures | 2683.5008 | t/a | 100%
Investment Data (Background Information) for COAL fired power plant
Conversion: | Conversion with currency exchange rate of author at given date into EUR, time conversion with CEPCI to 2010 afterwards | [12 empty] | CEPCI Factors | Factor | CEPCI Value
| Currency | Exchange Rate | Date | Reporting Country | [9 empty] | 2010 | 1 | 550.8
Nalbandian (IEA): | USD:EUR | 1.2 | 2006 | US | [9 empty] | 2009 | 1.0554 | 521.9
Brandwood (JEP): | EUR:GBP | 1.36 | 2007 | UK | [9 empty] | 2008 | 0.95725 | 575.4
[14 empty] | 2007 | 1.0483 | 525.4
Plant Electric Efficiency | 40% | Conversion kWe -> kWth | [11 empty] | 2006 | 1.1025 | 499.6
[14 empty] | 2005 | 1.1764 | 468.2
[14 empty] | 2004 | 1.24 | 444.2
|  | EUR / kWe |  | EUR / kWth |  |  | Given Literature Values | [6 empty] | 2003 | 1.3712 | 401.7
|  | Min | Max | Min | Max | Orignial Source | Min | Max | Unit | Country | Cost Year | Suppl. Info |  | 2002 | 1.3923 | 395.6
JEP | LNB+SNCR | 28.515 | 28.515 | 11.406 | 11.406 | Barmor, 2006 | 20 | 20 | GBP/kWe | UK | 2007 |  |  | 2001 | 1.3969 | 394.3
IEA | LNB | 2.3528 | 2.3528 | 5.8821 | 5.8821 | Orfanoudakis, 2005 | 5 | 5 | EUR/kWth | Greece | 2005 |  |  | 2000 | 1.3976 | 394.1
IEA | LNB | 5.8333 | 20.8333 | 2.3333 | 8.3333 |  | 7 | 25 | USD/kWe | UK |  | High End: OFA
IEA | LNB | 5.8333 | 30 | 2.3333 | 12 |  | 7 | 36 | USD/kWe | US |  | High End: OFA
IEA | LNB | 17.1397 | 17.1397 | 6.8559 | 6.8559 | Schneck, 2003 | 15 | 15 | USD/kWe | Canada | 2003
JEP | SCR | 114.0598 | 185.3472 | 45.6239 | 74.1389 | Literature Survey | 80 | 130 | GBP/kWe | US | 2007
JEP | SCR | 285.1496 | 299.4071 | 114.0598 | 119.7628 | Literature Survey | 200 | 210 | GBP/kWe | US | 2007 | Complicated
JEP | SCR | 47.6943 | 52.4172 | 19.0777 | 20.9669 | Literature Survey | 50 | 50 | EUR/kWe | France | 2007
JEP | SCR | 85.5449 | 114.0598 | 34.218 | 45.6239 | Barmor, 2006 | 60 | 80 | GBP/kWe | UK | 2007 | low eff. to high eff. SCR
IEA | SCR | 147.0525 | 205.8736 | 58.821 | 82.3494 | Orfanoudakis, 2005 | 50 | 70 | EUR/kWth | Greece | 2005
IEA | SCR | 50.5304 | 128.6229 | 20.2122 | 51.4492 |  | 55 | 140 | USD/kWe | US
IEA | SCR | 41.3431 | 82.6861 | 16.5372 | 33.0745 |  | 45 | 90 | USD/kWe | UK
IEA | SCR | 91.8735 | 91.8735 | 36.7494 | 36.7494 |  | 100 | 100 | USD/kWe | US
IEA | SCR | 79.9851 | 182.823 | 31.994 | 73.1292 | Morris, 2003 | 70 | 160 | USD/kWe | US | 2003 | Average 110 USD/kWe
IEA | SCR | 58.2044 | 128.0497 | 23.2818 | 51.2199 | US EPA, 2002 | 50 | 110 | USD/kWe | US | 2001 | US EPA Cost Methodology
IEA | SCR | 82.6655 | 123.9982 | 33.0662 | 49.5993 | US DOE, 2005 | 80 | 120 | USD/kWe | US | 2004
IEA | SNCR | 7.0585 | 14.117 | 17.6463 | 35.2926 | Orfanoudakis, 2005 | 15 | 30 | EUR/kWth | Greece | 2005
JEP | SNCR | 2.0386 | 2.0386 | 5.0965 | 5.0965 | SNCR recalculated by subtracting the LNB average from LNB+SNCR Investment of Barmor, 2006
|  |  |  | Lower | Upper
Total Average LNB | 6.3095 | EUR/kWth | EUR 2010 | 4.3512 | 8.2678
Total Average SCR | 48.7138 | EUR/kWth | EUR 2010 | 31.9581 | 55.5714
Total Average SNCR | 15.783 | EUR/kWth | EUR 2010 | 11.3714 | 20.1946
Old EGTEI Cost Function
| Constant | Linear Factor | Retrofit Factor | Year Factor 2000 -> 2010
| [1000 EUR] | [EUR/kWth] | % | Ratio
LNB | 780 | 2.15 | 0 | 1.3976
SCR | 5000 | 6.28 | 40% | 1.3976
Note on D12: Choose the "new" boiler outlet emission according to your preferred technology. For guiding, see Reference Box "NOx Boiler Outlet Emissions According to Plant Technology".
Note on D14: Gap closure between old boiler outlet emissions (spreadsheet emission calculation, cell D92) and new (retrofitted) boiler outlet emissions (cell D12) with respect to the corresponding ELV (cell D5).
Note on D19: No literature values could have been obtained
Note on D28: (Y) if you select ONE out of the two 2° abatement technologies, (N) if you select both. Please only select SCR or SNCR.

## Solid fuels_Fabric_Filter
Bottom up approach to define total filtration area | [8 empty] | Bottom up approach to define total filtration area - Reference Boxes
Reference box PJFF0 - By-products
[9 empty] | Sale prices range from 0.35 €/t to 6 €/t. In case of disposal, price is around 3.75 €/t. |  | Questionnaires
Fly ashes can be reused for cement production and public work applications.
By-products from PJFF
Commercial price in case of valorisation | -1 | €/t By-product
By-product disposal costs | 4 | €/t By-product | [6 empty] | Reference box PJFF1 - Air-to-Cloth ratio
[9 empty] | Air-to-Cloth ratio (cm/s) | 1,00-2,33 | Termokimik, E-On, Enel, Balcke Durr, Lurdi, Evonik
Which dust concentration (at stack) do you want to achieve? | [8 empty] | If PJFF is used after a dry FGD, then A/C should be in the following range : | 0,66-1,00 | Hamon
Dust stack concentration to be obtained | 20 | mg/Nm³, O2ref, dry
Current %-Gap to goal | 99.8785 | % | [6 empty] | Reference box PJFF2 - Conversion Net to Gross Cloth Area |  | US EPA
Inlet dust concentration | 16458.4567 | mg/Nm³, O2ref, dry | [6 empty] | Level of Net cloth Area (m²) | Multiplicator factor for gross cloth area
[9 empty] | 0 | 2
Air to cloth ratio for pulse jet fabric filter | [8 empty] | 370 | 1.5
Air to cloth ratio [A/C] | 0.013 | m/s | [6 empty] | 1115 | 1.25
Volumetric gas flow [vflue gasλ,dry] | 414.0672 | Nm³ Flue Gas,dry,λ / s | [6 empty] | 2230 | 1.17
Net cloth area [ANC] | 31852 | m2 | [6 empty] | 3350 | 1.125
Gross cloth area [AGC] | 33127 | m2 | [6 empty] | 4460 | 1.11
[9 empty] | 5580 | 1.1
[9 empty] | 6690 | 1.09
[9 empty] | 7810 | 1.08
[9 empty] | 8920 | 1.07
[9 empty] | 10040 | 1.06
[9 empty] | 12270 | 1.05
[9 empty] | 16730 | 1.04
Cost calculation | [8 empty] | Cost calculation - Reference boxes
Reference Box PJFF3 - Filter dimension
Baghouse division | [8 empty] | Compartment division | 1-30 | Duke Energy
Gross cloth area [AGC] | 33127 | m2 | [6 empty] | extra compartment | 0-2 | E-On, Enel
Number of compartments | 8
Compartment Area [Acomp] | 4140.875 | m2 | [6 empty] | Reference box PJFF4 - Price parameters for baghouse compartments - 2010 € |  |  |  | US EPA, 2002
Number of extra compartments | 2 | [7 empty] | Baghouse type | Component | a (€) | b (€/m2)
Total cloth area [Atot] | 41408.75 | m2 | [6 empty] | Pre-assembled unit | Basic unit | 55603.7574 | 123.5146 | Total cloth area should not exceed 2000 m² [Hamon]
[10 empty] | SS | 26789.4347 | 97.1198
[10 empty] | Insulation | 3087.6419 | 36.0565
Cost for baghouse compartments | [8 empty] | Field assembled unit | Basic unit | 422647.4529 | 89.6696
Compartment Area [Acomp] | 4140.875 | m2 | [7 empty] | SS | 143808.0273 | 33.9945 |  | 1
Pre-assembled unit or field assembled unit ? | Field assembled unit | [8 empty] | Insulation | 89878.9359 | 10.037 |  | 2
Basic unit | Y | Y
Stainless Steel | Y | Y/N
Thermal insulation | Y | Y/N
a1 | 422647.4529 | €
a2 | 143808.0273 | € | [6 empty] | Reference box PJFF5 - Bag cost factors for various materials
a3 | 89878.9359 | € | [6 empty] | PE | 1
b1 | 89.6696 | €/m2 | [6 empty] | CO | 1.125 | FF lesson 4
b2 | 33.9945 | €/m2 | [6 empty] | PP | 1.2 | Balcke Durr
b3 | 10.037 | €/m2 | [6 empty] | FG | 2.5 | FF lesson 4
Cost for baghouse compartments | 12099741.9914 | € | [6 empty] | NO | 5 | FF lesson 4
[9 empty] | RT | 6.25 | FF lesson 4
[9 empty] | P8 | 7.5 | FF lesson 4
Bags cost | [8 empty] | TF | 9.4 | Balcke Durr ; Entretien industriel CITEPA
Media material | RT
Reference price for PE material | 9 | €/m2
Bag prices [Cbagarea] | 56.25 | €/m2 | [6 empty] | Reference Box PJFF6 - Price Utilities
Bags cost [Cbagtotal] | 2329242.1875 | € | [6 empty] | PE media price (€/m2) | 5-9
[9 empty] | Cage price (€/m2 filtering media) | 16-25 | US EPA 2002
Cage cost for pulse jet application | [8 empty] | Reference Box PJFF7 - Filter dimension
Lenght | 8 | m | [6 empty] | Lenght (m) | 3-9 | E-On Engineering
Diameter | 150 | mm | [6 empty] | Diameter (mm) | 120-180 | Hamon
Cage price per m2 filtering media | 20 | €/m2 filtering media
Total cage cost | 828175 | €
Economic Analysis | [8 empty] | Economic Analysis - Reference Boxes
Economic Analysis
Dust emissions avoided | 246413.2881 | t/a
Equipment cost | 17545733.0557 | € | [6 empty] | Reference Box PJFF8 - Data Utilities
Direct installation cost | 12983842.4612 | € | [6 empty] | Pressure drop range (mbar) | 25 - 50 | Duke Energy
Indirect installation cost | 7895579.8751 | € | [6 empty] | Fan efficiency range (%) | 40-70 | US EPA
Is it a new combustion plant? | N | Y/N | [6 empty] | Bag life (operating hour) | 15 000-40 000 | E-On, Enel
Is there valorisation of by-products? | Y | Y/N | [6 empty] | Compressed to actual air flow ratio | 0.002 | US EPA
Total Investment | 45443448.6143 | €
Capital Cost p.a. | 4087233.773 | €/a | [6 empty] | Reference Box PJFF9 - Purchase equipment factors |  | US EPA
Operating Costs | [8 empty] | Instrumentation | 0.1
Fixed O&M Costs | 908868.9723 | €/a | [6 empty] | Freight | 0.05
Variable Operating Costs
Pressure drop value | 50 | mbar
Fan efficiency | 65% | % | [6 empty] | Reference Box PJFF10 - Direct installation factors
Fan utility electricity consumption | 3.1693 | MWh/h | [6 empty] | Foundation & support | 0.04
Compressed to actual air flow ratio | 0.002 | [7 empty] | Handling and erection | 0.5
Air compressor consumption | 1.118 | MWh/h | [6 empty] | Electrical | 0.08
Bag-lifetime | 20000 | hours | [6 empty] | Piping | 0.01
By-Product management cost | -246413.2881 | €/a | [6 empty] | Insulation for ductwork | 0.07
Utility electricity cost | 2253411.3528 | €/a | [6 empty] | Painting | 0.04
Bag replacement cost [Crepbags] | 1129335.4171 | €/a
Total variable costs | 3136333.4818 | €/a | [6 empty] | Reference Box PJFF11 - Indirect installation factors
[9 empty] | Engineering | 0.1
Summary for PJFF | [8 empty] | Construction and filed expense | 0.2
TSP emissions avoided | 246413.2881 | t TSP/year | [6 empty] | Contractor fees | 0.1
Inlet TSP concentrations | 16458.4567 | mg/Nm³ TSP, dry, ref O2-% | [6 empty] | Start-up | 0.01
Outlet TSP concentrations | 20 | mg/Nm³ TSP, ref O2-% | [6 empty] | Performance test | 0.01
Efficiency required | 99.8785 | % | [6 empty] | Contingencies | 0.03
Total investment | 45443448.6143 | €
Total annual costs | 8132436.2271 | €/year
Spec.TSP reduction cost | 33.0032 | €/t TSP abated
Spec. investment per kWth | 36.3548 | €/kWth
Electricity penalty | 0.85746 | %
Share capital costs to total costs | 50.26%
Share operating costs to total costs | 49.74%
Investment Data (Background Information)
Conversion: | Conversion with currency exchange rate at given date into EUR, time conversion with CEPCI to 2010 afterwards
Plant Electric Efficiency | 40% | Conversion kWe -> kWth
Literature | Cost Year | Currency year / power unit |  |  |  |  | EURO 2010 / kWth
|  | Min | Max | Currency |  | Power unit | Min | Max
RAINS | 2005 | 23.8 | 23.8 | £ | / | kWe | 16.3736 | 16.3736
AEP | 2005 | 28 | 28 | £ | / | kWe | 19.263 | 19.263
Nalbandian [Smith] | 2006 | 53 | 80 | $ | / | kWe | 18.6088 | 28.0887
Naldandian [Orfanoudakis] | 2006 | 60.5 | 60.5 | $ | / | kWe | 21.2421 | 21.2421
Nalbandian | 2006 | 60 | 60 | $ | / | kWe | 21.0665 | 21.0665
World bank | 2001 | 36 | 36 | $ | / | kWe | 22.4332 | 22.4332
IEA | 1998 | 50 | 70 | $ | / | kWe | 25.2296 | 35.3215
Balcke Durr | 2008 | 19.7 | 21 | € | / | kWth | 18.8578 | 20.1022
PM BART determination [American Electric Power] | 2007 | 50 | 50 | $ | / | kWe | 38.2328 | 38.2328
Sargent et Lundy | 2010 | 65.2069 | 87.5554 | $ | / | kWe | 18.7376 | 25.1596
IEA | 2000 | 4.8 | 45 | $ | / | kWth | 7.2603 | 68.0657
Wu | 2001 | 3.9 | 16.5 | $ | / | kWth | 6.0803 | 25.7243
Note on D8: A negative figure is input due to benefit in case of valorisation

## Solid fuels_ESP
Bottom up approach to define Effective Collecting Plate Area | [8 empty] | Bottom up approach to define Effective Collecting Plate Area - Reference Boxes
By-products from ESP | [9 empty] | Reference box 0 ESP - By-products
Commercial price in case of valorisation | -1 | €/t By-product | [7 empty] | Sale prices range from 0.35 €/t to 6 €/t. In case of disposal, price is around 3.75 €/t. |  |  | questionnaires
By-product disposal costs | 4 | €/t By-product | [7 empty] | Fly ashes can be reused for cement production and public work applications.
Which dust concenration (at stack) do you want to achieve?
Dust stack concentration to be obtained | 20 | mg/Nm³, O2ref, dry
Current %-Gap to goal | 99.8785 | %
Inlet dust concentration | 16458.4567 | mg/Nm³, O2ref, dry
Method for A ECP determination
Back corona | N | Y/N | [7 empty] | Reference box ESP-1 Values for A ECP determination
Temperature [T] | 400 | K | [7 empty] | Parameter | Value | Unit | Source | US EPA 2002
Mass mean Diameter [MMDin] | 20 | µm | [7 empty] | Temperature [T] | 410-500 | K
Design penetration | 0.0012152 | [8 empty] | Mass mean Diameter [MMDin] | [4-21] | µm
Gas viscosity [μG] | 2.2559e-05 | kg/m/s | [7 empty] | Sneakage [SN] | 0.07
Electric field at sparking [Ebd] | 335436.2014 | V/m |  | n | MMDi | SCA (s/m) |  |  |  | Raping reentrainment [RR] | 0.14
E avg | 191677.8294 | V/m |  | 1 | 20 | 8.3085 |  |  |  | Most penetrating size [MMDp] | 2 | µm
n | 5 |  |  | 2 | 8.6474 | 19.2163 |  |  |  | Rapping puff size [MMDr] | 5 | µm
Average section penetration [ps] | 0.26117 |  |  | 3 | 5.352 | 31.0485 |  |  |  | Free space permittivity [ε0] | 8.845e-12 | F/m
Section collection penetration [pc] | 0.076235 |  |  | 4 | 4.3954 | 37.8055 |  |  |  | Loss factor [LF] | 0.2002
D | 0.26117 |  |  | 5 | 4.1177 | 40.3548
MMDrp | 2.3026 | µm |  | 6
[SCA] | 136.7337 | s/m
dry flue gas volume per second [vflue gasλ,dry,sec] | 414.0672 | Nm³ Flue Gas,dry,λ /sec
Effective Collecting Plate Area [AECP] | 56616.9461 | m2
Economic Analysis | [8 empty] | Economic Analysis - Reference Boxes
Economic Analysis
Dust emissions saved | 246413.2881 | t/a | [8 empty] | Reference box ESP-2 Equipment cost in 2010 €
With option | Y | Y/N | [8 empty] | Plate area inferior limit (m2) | a | b | US EPA, Lesson 3
Effective Collecting Plate Area [AECP] | 56616.9461 | m2 | [7 empty] | Basic unit | AECP ≤ 4645 m2 | 3495.68 | 0.6275 |  | Basic unit | 1
a | 796.16 | €/m2 | [8 empty] | AECP > 4645 m2 | 549.12 | 0.8431 |  | All standard option | 2
b | 0.8431 | [8 empty] | All standard option | AECP ≤ 4645 m2 | 5068.8 | 0.6276
ESP material | Stainless steel 304 | [9 empty] | AECP > 4645 m2 | 796.16 | 0.8431
SO3 injection precaution | Y
Equipment cost | 14401820.0492 | € | [8 empty] | Reference box ESP-3 cost using various materials |  | US EPA
Direct installation cost | 9649219.4329 | € | [8 empty] | Material | Factor
Indirect installation cost | 8209037.428 | € | [8 empty] | Carbon Steel | 1
Is it a new combustion plant? | N | Y/N | [8 empty] | Stainless steel 304 | 1.3
Is there valorisation of by-products? | Y | Y/N | [8 empty] | Stainless steel 316 | 1.7
[11 empty] | Carpenter 20 CB-3 | 1.9
Total Investment | 38020804.9298 | € | [8 empty] | Monel-400 | 2.3
Capital Cost p.a. | 3419633.0324 | €/a | [8 empty] | Nickel-200 | 3.2
Operating Costs | [10 empty] | Titanium | 4.5
Fixed O&M Costs | 760416.0986 | €/a
Variable Operating Costs
Pressure drop value | 25 | mbar
Fan efficiency | 65% | %
Fan utility electricity consumption | 1.5847 | MWh/h | [8 empty] | Reference Box ESP-4 Calculated Utilities
ESP power requirement | 1.1833 | MWh/h | [8 empty] | Pressure drop range (mbar) | 25 - 50 | US EPA, Zevenhoven & Kilpinen
Utility electricity cost | 1454839.5669 | €/a | [8 empty] | Fan efficiency range (%) | 40-70 | US EPA
SO3 injection rate | 35 | kg/h
SO3 consumption cost | 21462 | €/a | [10 empty] | Us EPA 2002
By-Product management cost | -246413.2881 | €/a | [8 empty] | Reference Box ESP-5 Purchase equipment factors
Total variable costs | 1990304.3775 | €/a | [8 empty] | Instrumentation | 0.1
[11 empty] | Freight | 0.05
Summary for PJFF
TSP emissions avoided | 246413.2881 | t TSP/year | [8 empty] | Reference Box ESP-5 Direct installation factors
inlet TSP concentrations | 16458.4567 | mg/Nm³ TSP, dry, ref O2-% | [8 empty] | Foundation & support | 0.04
outlet TSP concentrations | 20 | mg/Nm³ TSP, ref O2-% | [8 empty] | Handling and erection | 0.5
Efficiency required | 99.8785 | % | [8 empty] | Electrical | 0.08
Total investment | 38020804.9298 | € | [8 empty] | Piping | 0.01
Total annual costs | 5409937.4098 | €/year | [8 empty] | Insulation for ductwork | 0.02
Spec.TSP reduction cost | 21.9547 | €/t TSP abated | [8 empty] | Painting | 0.02
Spec. investment per kWth | 30.4166 | €/kWth
Electricity penalty | 0.31693 | % | [8 empty] | Reference Box ESP6- Indirect installation factors
Share capital costs to total costs | 63.21% | [9 empty] | Engineering | 0.2
Share operating costs to total costs | 36.79% | [9 empty] | Construction and field expenses | 0.2
[11 empty] | Contractor fees | 0.1
[11 empty] | Start-up | 0.01
[11 empty] | Performance test | 0.01
[11 empty] | Model Study | 0.02
[11 empty] | Contingencies | 0.03
[11 empty] | Reference Box ESP-6 SO3 conditionning |  | Evonik, ESP performance enhancements by SO3 conditioning-2011
[11 empty] | SO3 injection rate (kg/h) | 10-80
[11 empty] | Sulfur cost (€/t) | 70
Investment Data (Background Information)
Conversion: | Conversion with currency exchange rate at given date into EUR, time conversion with CEPCI to 2010 afterwards
Plant Electric Efficiency | 40% | Conversion kWe -> kWth
Literature | Cost Year | Currency year / power unit |  |  |  |  | EURO 2010 / kWth
|  | Min | Max | Currency |  | Power unit | Min | Max
RAINS | 2005 | 17.3 | 17.3 | £ | / | kWe | 11.9018 | 11.9018
AEP | 2005 | 32 | 36 | £ | / | kWe | 22.0149 | 24.7667
Nalbandian | 2006 | 70.7 | 70.7 | $ | / | kWe | 24.8234 | 24.8234
Naldandian [Orfanoudakis] | 2006 | 85 | 85 | $ | / | kWe | 29.8443 | 29.8443
World bank | 2001 | 29 | 33 | $ | / | kWe | 18.0712 | 20.5638
IEA | 1998 | 40 | 60 | $ | / | kWe | 20.1837 | 30.2756
Balcke Durr | 2008 | 25.8 | 41.8 | € | / | kWth | 24.697 | 40.0129
Questionnary Plant D | 1983 | 13.3 | 13.3 | € | / | kWth | 23.3301 | 23.3301
Zevenhoven & Kilpinen | 1982 | 9.65 | 9.65 | $ | / | kWth | 17.2782 | 17.2782
Rubin | 1985 | 43 | 43 | $ | / | kWe | 38.3199 | 38.3199
Sankey | 1997 | 19 | 19 | $ | / | kWth | 23.8562 | 23.8562
IEA | 1995 | 9 | 30 | $ | / | kWth | 9.9447 | 33.1489
Note on D5: A negative figure is input due to benefit in case of valorisation

## Liquid fuels_ESP
Bottom up approach to define Effective Collecting Plate Area | [8 empty] | Bottom up approach to define Effective Collecting Plate Area - Reference Boxes
By-products from ESP
Commercial price in case of valorisation | -1 | €/t By-product | [7 empty] | Reference box 0 ESP - By-products
By-product disposal costs | 4 | €/t By-product | [7 empty] | Sale prices range from 0.35 €/t to 6 €/t. In case of disposal, price is around 3.75 €/t. |  |  | questionnaires
Fly ashes can be reused for cement production and public work applications.
Which dust concentration (at stack) do you want to achieve?
Dust stack emission to be obtained | 20 | mg/Nm³, O2ref, dry
Current %-Gap to goal | 75.3594 | %
Inlet dust concentration | 81.167 | mg/Nm³,02 ref,dry
Method for A ECP determination
Back corona | N | Y/N | [7 empty] | Reference box ESP-1 Values for A ECP determination
Temperature [T] | 430 | K | [7 empty] | Parameter | Value | Unit | Source | US EPA 2002
Mass mean Diameter [MMDin] | 30 | µm | [7 empty] | Temperature [T] | 410-500 | K
Design penetration | 0.24641 | [8 empty] | Mass mean Diameter [MMDin] | [4-21] | µm
Gas viscosity [μG] | 2.3747e-05 | kg/m/s | [7 empty] | Sneakage [SN] | 0.07
Electric field at sparking [Ebd] | 297704.888 | V/m |  | n | MMDi | SCA (s/m) |  |  |  | Raping reentrainment [RR] | 0.14
E avg | 170117.0789 | V/m |  | 1 | 30 | 8.2001 |  |  |  | Most penetrating size [MMDp] | 2 | µm
n | 1 |  |  | 2 | 11.8601 | 20.7422 |  |  |  | Rapping puff size [MMDr] | 5 | µm
Average section penetration [ps] | 0.24641 |  |  | 3 | [5 empty] | Free space permittivity [ε0] | 8.845e-12 | F/m
Section collection penetration [pc] | 0.057772 |  |  | 4 | [5 empty] | Loss factor [LF] | 0.2002
D | 0.24641 |  |  | 5
MMDrp | 2.4894 | µm |  | 6
[SCA] | 28.9423 | s/m
dry flue gas volume per second [vflue gasλ,dry,sec] | 383.7262 | Nm³ Flue Gas,dry,λ / s
Effective Collecting Plate Area [AECP] | 11105.9269 | m2
Economic Analysis | [8 empty] | Economic Analysis - Reference Boxes
Economic Analysis
Dust emissions saved | 707.1117 | t/a | [8 empty] | Reference box ESP-2 Equipment cost in 2010 €
With option | Y | Y/N | [8 empty] | Plate area inferior limit (m2) | a | b | US EPA, Lesson 3
Effective Collecting Plate Area [AECP] | 11105.9269 | m2 | [7 empty] | Basic unit | AECP ≤ 4645 m2 | 3495.68 | 0.6275 |  | Basic unit | 1
a | 796.16 | €/m2 | [8 empty] | AECP > 4645 m2 | 549.12 | 0.8431 |  | All standard option | 2
b | 0.8431 | [8 empty] | All standard option | AECP ≤ 4645 m2 | 5068.8 | 0.6276
ESP material | Stainless steel 304 | [9 empty] | AECP > 4645 m2 | 796.16 | 0.8431
SO3 injection precaution | Y
Equipment cost | 5365129.3479 | € | [8 empty] | Reference box ESP-3 cost using various materials |  | US EPA
Direct installation cost | 3594636.6631 | € | [8 empty] | Material | Factor
Indirect installation cost | 3058123.7283 | € | [8 empty] | Carbon Steel | 1
Is it a new combustion plant? | Y | Y/N | [8 empty] | Stainless steel 304 | 1.3
Is there valorisation of by-products? | Y | Y/N | [8 empty] | Stainless steel 316 | 1.7
[11 empty] | Carpenter 20 CB-3 | 1.9
Total Investment | 12017889.7392 | € | [8 empty] | Monel-400 | 2.3
Capital Cost p.a. | 1080902.2273 | €/a | [8 empty] | Nickel-200 | 3.2
Operating Costs | [10 empty] | Titanium | 4.5
Fixed O&M Costs | 240357.7948 | €/a
Variable Operating Costs
Pressure drop value | 25 | mbar
Fan efficiency | 65% | %
Fan utility electricity consumption | 1.4685 | MWh/h | [8 empty] | Reference Box ESP-4 Calculated Utilities
ESP power requirement | 0.23211 | MWh/h | [8 empty] | Pressure drop range (mbar) | 25 - 50 | US EPA, Zevenhoven & Kilpinen
Utility electricity cost | 536320.7624 | €/a | [8 empty] | Fan efficiency range (%) | 40-70 | US EPA
SO3 injection rate | 35 | kg/h
SO3 consumption cost | 12877.2 | €/a | [10 empty] | Us EPA 2002
By-Product management cost | -707.1117 | €/a | [8 empty] | Reference Box ESP-5 Purchase equipment factors
Total variable costs | 788848.6455 | €/a | [8 empty] | Instrumentation | 0.1
[11 empty] | Freight | 0.05
Summary for PJFF
TSP emissions avoided | 707.1117 | t TSP/year | [8 empty] | Reference Box ESP-5 Direct installation factors
Inlet TSP concentrations | 81.167 | mg/Nm³ TSP, dry, ref O2-% | [8 empty] | Foundation & support | 0.04
Outlet TSP concentrations | 20 | mg/Nm³ TSP, ref O2-% | [8 empty] | Handling and erection | 0.5
Efficiency required | 75.3594 | % | [8 empty] | Electrical | 0.08
Total investment | 12017889.7392 | € | [8 empty] | Piping | 0.01
Total annual costs | 1869750.8728 | €/year | [8 empty] | Insulation for ductwork | 0.02
Spec.TSP reduction cost | 2644.2088 | €/t TSP abated | [8 empty] | Painting | 0.02
Spec. investment per kWth | 9.6143 | €/kWth
Electricity penalty | 0.29371 | % | [8 empty] | Reference Box ESP6- Indirect installation factors
Share capital costs to total costs | 57.81% | [9 empty] | Engineering | 0.2
Share operating costs to total costs | 42.19% | [9 empty] | Construction and field expenses | 0.2
[11 empty] | Contractor fees | 0.1
[11 empty] | Start-up | 0.01
[11 empty] | Performance test | 0.01
[11 empty] | Model Study | 0.02
[11 empty] | Contingencies | 0.03
[11 empty] | Reference Box ESP-6 SO3 conditioning |  | Evonik, ESP performance enhancements by SO3 conditioning-2011
[11 empty] | SO3 injection rate (kg/h) | 10-80
[11 empty] | Sulfur cost (€/t) | 70
Investment Data (Background Information)
Conversion: | Conversion with currency exchange rate at given date into EUR, time conversion with CEPCI to 2010 afterwards
Plant Electric Efficiency | 40% | Conversion kWe -> kWth
Literature | Cost Year | Currency year / power unit |  |  |  |  | EURO 2010 / kWth
|  | Min | Max | Currency |  | Power unit | Min | Max
RAINS | 2005 | 17.3 | 17.3 | £ | / | kWe | 11.9018 | 11.9018
AEP | 2005 | 32 | 36 | £ | / | kWe | 22.0149 | 24.7667
Nalbandian | 2006 | 70.7 | 70.7 | $ | / | kWe | 24.8234 | 24.8234
Naldandian [Orfanoudakis] | 2006 | 85 | 85 | $ | / | kWe | 29.8443 | 29.8443
World bank | 2001 | 29 | 33 | $ | / | kWe | 18.0712 | 20.5638
IEA | 1998 | 40 | 60 | $ | / | kWe | 20.1837 | 30.2756
Balcke Durr | 2008 | 25.8 | 41.8 | € | / | kWth | 24.697 | 40.0129
Questionnary Plant D | 1983 | 13.3 | 13.3 | € | / | kWth | 23.3301 | 23.3301
Zevenhoven & Kilpinen | 1982 | 9.65 | 9.65 | $ | / | kWth | 17.2782 | 17.2782
Rubin | 1985 | 43 | 43 | $ | / | kWe | 38.3199 | 38.3199
Sankey | 1997 | 19 | 19 | $ | / | kWth | 23.8562 | 23.8562
IEA | 1995 | 9 | 30 | $ | / | kWth | 9.9447 | 33.1489
Note on D5: A negative figure is input due to benefit in case of valorisation

## Solid fuels_DeSO2
Details on SO2 abatement techniques | [7 empty] | Details on SO2 abatement techniques - Reference Boxes
Which SO2 concentration (at stack) do you want to achieve?
SO2 stack concentration target | 200 | mg/Nm³, ref O2, dry | [5 empty] | Reference Box 1 - reagents
Current %-Gap to goal | 84.7499 | %
Inlet SO2 concentration | 1311.471 | mg/Nm³, ref O2, dry | [5 empty] | CaCO3 purity may range from 90 to 98 %. From questionnaires 94 to 96 % are observed in 4 plants
Reagent and by-product characteristics and prices | [7 empty] | CaCO3 prices depend on quantity bought and quality. From questionnaires, prices range from : |  |  | Questionnaires
Purity of limestone for LSFO FGD | 96 | % | see reference box 1, reagents |  |  |  |  | 11 to 16 €/CaCO3 in a 2465 MWth plant and 32 to 36€/t CaCO3 in a 630 MWth plant
Price of limestone for LSFO FGD | 40 | €/t CaCO3 | [5 empty] | and 40 €/t CaCO3 in another 630 MWth plant for similar purity of CaCO3 (94 % to 96 %)
Purity of lime for LSD FGD | 96 | %
Price of lime for LSD FGD | 80 | €/t CaO | [5 empty] | Quicklime or CaO used in LSD FGD has a purity range from |  | 93 % is encountered | Sargent and Lundy 2007
Purity of lime for DSI FGD | 96 | % | [5 empty] | Price is about 5 times price of limestone. Price range is 80 to 150 €/t CaO according to the specific surface
Price of lime for DSI FGD | 80 | €/t CaO | [5 empty] | Price and purity to be completed for sodium bicarbonate
Use of Sodium bicarbonate for DSI FGF | N | Y/N
Purity of sodium bicarbonate for DSI FGD | 96 | %
Price of sodium bicarbonate for DSI FGD | 80 | €/t sodium bicarbonate
By-products from LSFO FGD | [7 empty] | Reference Box 2 - by-products |  |  |  | Reference Box 2 (following) - by-products
Commercial price in case of valorisation | -0.15 | €/t By-product | see reference box 2, by products |  |  |  |  | LSFO FGD: commercial-grade gypsum price depends on chlorine content, purity, colour. |  |  |  | LSD and DSI FDG:
By-product disposal (or other destination) costs | 20 | €/t By-product | [5 empty] | Commercial grade gypsum can be used in wallboard, cement or plaster manufacturing, also soil |  |  |  | If collected separately from fly ash, in case of retrofit and use of the ESP in place, dry by-product may be
By-products from LSD FGD | [7 empty] | conditioner. Price can be low due to saturation of the market. Questionnaires provide a range between |  |  |  | land filled or used as soil conditioner.
Commercial price in case of valorisation | 0 | €/t By-product | [5 empty] | 0.15 to 2 €/t by-product. |  |  |  | The predominant mode of dry FGD by-product elimination is disposal as fly ash separation is in fact
By-product disposal costs | 20 | €/t By-product | [5 empty] | Disposal prices depend on the waste disposal treatment. Landfill or other treatment such as incineration. |  |  |  | rarely done.
By-products from DSI FGD | [7 empty] | By product prices range from 0.33 to 89 €/t by-product according to the questionnaires obtained. |  |  |  | According to one expert, cost for waste disposal may reach 200 €/t bp due to the fact the product is in a
From lime | [11 empty] | pulverised dry form
Commercial price in case of valorisation | 0 | €/t By-product | [9 empty] | When sold to the cement industry if the product is without fly ash, a positive cost may be encountered,
By-product disposal costs | 40 | €/t By-product | [9 empty] | 40 €/t bp
From sodium bicarbonate
Commercial price in case of valorisation
By-product disposal costs
Choice of the emission reduction technique
Primary Measures
Do you want to use a lower sulphur content coal? | y | Yes/No | See reference box 3 - sulphur content of coals and prices
What is the sulphur content of the low sulphur coal? | 0.4 | % Sulphur w/w waf | still provisional
Concentration achieved with low sulphur content fuel | 728.595 | mg/Nm³, ref O2, dry
Gap-Closure to emission goal (% of Cell D7) | 52.4419 | %
Reduction required with secondary measure | 72.5499 | %
[8 empty] | Reference box 3 - sulphur content of coal and prices |  |  |  | Reference box 4 - FGD efficiency and range of application
Secondary Measures | [7 empty] | the sulphur content can be as low as 0,37 % w/w? |  |  |  | LSD FGD typically used for : | plant lower than (MWth) | 1500 | Sargent and Lundy 2007
Inlet SO2 concentrations | 728.595 | mg/Nm³, ref O2, dry | See reference box 4 - FGD efficiency and range of application |  |  |  |  | Coal 2% S prices range from |  | €/t |  |  | low and medium sulphur content fuels | < 1.5 % | Nalbandian 2006
Do you want to estimate costs for LSFO FGD? | Y | Yes/No | [5 empty] | Coal 1% S prices range from | 100 | €/t |  | Its efficiency can reach : |  | 90 to 95 % | Sargent and Lundy 2007
Do you want to estimate costs for LSD FGD? | Y | Yes/No |  |  |  | 0.014286 |  | Coal 0.5% S prices range from |  | €/t |  | LSFO FGD can be applied | for all sizes of plant but is preferably used for the largest ones |  | Sargent and Lundy 2007
Do you want to estimate costs for DSI FGD? | y | Yes/No | [5 empty] | Coal 0.3 % S prices range from |  | €/t |  |  | all sulphur contents | All sulphur content
New SO2 outlet emissions | 200 | mg/Nm³, ref O2, dry | [5 empty] | Coal factor is 1 for coals and 1.07 for lignites |  |  |  | Its efficiency can reach : |  | 99% | Sargent and Lundy 2007, Nalbandian 2006
Total reduction required | 72.5499 | %
Degree of Over-Achievement to ELV | 0 | % | [5 empty] | Reference box 5 - retrofit factor
Retrofit factor | 1 |  | See reference box 5 - retrofit factor |  |  |  |  | retrofit factor can range from 1 to 1.4 in case of very congested site |  |  | Nalbandian 2006
Coal factor | 1 |  | See reference box 3 - sulphur content of coals and prices
| Coal Fuel Spec. Used: |  | Biomass Fuel Spec. Used |  |  | Co-Firing Fuel Spec. Used
Lower Heating Value [LHVfuel] | 22.4435 | MJ/kg LHV | 10 | MJ/kg LHV |  | Lower Heating Value [LHVfuel] | 22.4435 | MJ/kg LHV
Sulphur mass fraction [xS] | 0.4 | % Sulphur w/w waf | 0.1 | % Sulphur w/w waf |  | Sulphur mass fraction [xS] | 0.4 | % Sulphur w/w waf
Ash mass fraction [xash] | 14.49 | % Ash | 2 | % Ash |  | Ash mass fraction [xash] | 14.49 | % Ash
Moisture mass fraction [xmoist] | 7.71 | % Moisture | 25 | % Moisture |  | Moisture mass fraction [xmoist] | 7.71 | % Moisture
Spec. wet flue gas volume [vflue gasλ,wet] | 7.9438 | Nm³ Flue Gas,wet,λ /kg Coal | 3.7588 | Nm³ Flue Gas,wet,λ /kg Biomass |  | Spec. wet flue gas volume [vflue gasλ,wet] | 7.9438 | Nm³ Flue Gas,wet,λ /kg Fuel
Annual wet flue gas volume [vflue gasλ,wet,year] | 13952545236.5953 | Nm³ Flue Gas,wet,λ / year | 14817211500 | Nm³ Flue Gas,wet,λ / year |  | Annual wet flue gas volume [vflue gasλ,wet,year] | 13952545236.5953 | Nm³ Flue Gas,wet,λ / year
Spec. dry flue gas volume [vflue gasλ,dry] | 7.4345 | Nm³ flue gas,dry,λ / kg Coal | 3.0059 | Nm³ flue gas,dry,λ / kg Biomass |  | Spec. dry flue gas volume [vflue gasλ,dry] | 7.4345 | Nm³ flue gas,dry,λ / kg Fuel
Annual dry flue gas volume [vflue gasλ,dry,year] | 13058023445.1561 | Nm³ Flue Gas,dry,λ / year | 11849376628.3599 | Nm³ Flue Gas,dry,λ / year |  | Annual dry flue gas volume [vflue gasλ,dry,year] | 13058023445.1561 | Nm³ Flue Gas,dry,λ / year
Oxygen concentration [cO2,act] | 3.7806 | % O2, dry | 4.3419 | % O2, dry |  | Oxygen concentration [cO2,act] | 3.7806 | % O2, dry
Oxygen correction factor [fO2,corr] | 0.87111 | O2 corr. Factor to ref. O2 | 0.90046 | O2 corr. Factor to ref. O2 |  | Oxygen correction factor [fO2,corr] | 0.87111 | O2 corr. Factor to ref. O2 %
SO2 boiler outlet emissions [loadboSO2,dry,ref O2] | 728.595 | mg/Nm³ SO2, dry, ref O2 | 436.9519 | mg/Nm³ SO2, dry, ref O2 |  | SO2 boiler outlet emissions [loadboSO2,dry,ref O2] | 728.595 | mg/Nm³ SO2, dry, ref O2-%
Sulphur mass fraction [x real S] | 0.3112 | % Sulphur w/w real | 0.073 | % Sulphur w/w real |  | Sulphur mass fraction [x real S] | 0.3112 | % Sulphur w/w real
SO2 boiler outlet emissions [loadboSO2] | 0.27706 | kg SO2/GJ | 0.14586 | kg SO2/GJ |  | SO2 boiler outlet emissions [loadboSO2] | 0.27706 | kg SO2/GJ
Gross heat rate [GHR] | 0.009 | GJ/kWh | 0.009 | GJ/kWh |  | Gross heat rate [GHR] | 0.009 | GJ/kWh
Economic Analysis | [7 empty] | Economic Analysis - Reference Boxes
Primary Measures - Low sulphur fuels
SO2 emissions saved | 8737.3406 | t SO2/year
Spec. Additional cost of low sulphur coal | 5 | €/t coal | See reference box 3 - sulphur content of coals and prices
Total Investment | No investment | €
Capital Cost p.a. | No capital cost | €/year
Annual additional costs | 8782057.5818 | €/year
| 1756411.5164 | t coal/year
Total annual costs | 8782057.5818 | €/year
Spec. SO2 reduction costs | 1005.1179 | €/t SO2
Secondary Measures - LSFO FGD (if LSFO FGD = Y)
LSFO FGD (Y/N) | Y
SO2 emissions saved | 7923.6658 | t SO2/year
Is there valorisation of waste | Y | Y/N | [5 empty] | Reference box 6 - investment
Capital Costs | [7 empty] | Investment function derived from Sargent and Lundy 2010
Absorber unit cost | 30014841.6911 | € | see reference box 6: investment
Reagent preparation unit cost | 9747533.3786 | €
Waste handling unit cost | 4689341.7279 | €
Base balance plant cost | 58201428.1543 | €
Total cost for LSFO FGD unit | 102653144.9519 | €
Indirect installation cost | 30795943.4856 | €
Home office cost | 6672454.4219 | €
Total investment cost | 140121542.8593 | €
Capital Cost p.a. | 12602685.7504 | €/year
Operating Costs | [7 empty] | Reference Box 7 - Fixed operating cost
Fixed O&M Costs | 1793650.408 | €/year | See reference Box 7 - Fixed operating cost
[8 empty] | Fixed operating cost ratio | 2.5 | % | Sargent and Lundy 2010
Variable Operating costs
Reagent price | 40 | €/ton CaCO3 | see reference box 1, reagents
Specific limestone demand | 1.2283 | t CaCO3/t SO2
Reagent consumption | 9732.8892 | t CaCO3/year
Reagent cost | 389315.5683 | €/year
Electricity price | 60 | €/MWh
Electricity consumption | 61039.68 | MWh/year
Electricity cost | 3662380.8 | €/year
By-product price | -0.15 | €/ton By-product | See reference Box 2 - by-products
By-product generated | 2.3014 | t By-product/t SO2 abated
By-product amount | 18235.5412 | t By-product/year
By-product management cost | -2735.3312 | €/year
Annual operating costs | 5842611.4451 | €/year
Summary for LSFO FGD
SO2 emissions avoided | 7923.6658 | t SO2/year
Outlet SO2 concentrations obtained | 200 | mg/Nm³ SO2, dry, ref O2-%
Inlet SO2 concentrations | 728.595 | mg/Nm³ SO2, dry, ref O2-%
Efficiency required | 72.5499 | %
Total investment | 140121542.8593 | €
Total annual costs | 18445297.1956 | €/year
Spec.SO2 reduction cost | 2327.8742 | €/t SO2 abated
Spec. investment per kWth | 112.0972 | €/kWth
Electricity penalty | 1.3936 | %
Share capital costs to total costs | 68.32%
Share operating costs to total costs | 31.68%
Summary for low sulphur fuel and LSFO FGD
SO2 emissions avoided | 16661.0064 | t SO2/year
Outlet SO2 concentrations obtained | 200 | mg/Nm³ SO2, dry, ref O2-%
Inlet SO2 concentrations | 1311.471 | mg/Nm³ SO2, dry, ref O2-%
Efficiency required | 84.7499 | %
Total investment | 140121542.8593 | €
Total annual costs | 27227354.7773 | €/year
Spec.SO2 reduction cost | 1634.1963 | €/t SO2 abated
Spec. investment per kWth | 112.0972 | €/kWth
Electricity penalty | 1.3936 | %
Share capital costs to total costs | 46.29%
Share operating costs to total costs | 53.71%
Secondary Measures - LSD FGD (if LSD FGD = Y)
LSD FGD (Y/N) | Y | Y/N
SO2 emissions saved | 7923.6658 | t SO2/year
Is there valorisation of waste | N | y/n
Capital Costs
Absorber unit cost | 31024305.8861 | € | see reference box 6: investment
Reagent preparation and waste handling units cost | 16341130.2942 | €
Base balance plant cost | 46042509.4327 | €
Total cost for LSD FGD unit | 93407945.613 | €
Indirect installation cost | 28022383.6839 | €
Home office cost | 6071516.4648 | €
Total investment cost | 127501845.7617 | €
Capital Cost p.a. | 11467656.3071 | €/year
Operating Costs
Fixed O&M Costs | 1896592.3255 | €/year | See reference Box 7 - Fixed operating cost
Reagent price | 80 | € / ton CaO | see reference box 1, reagents
Specific reagent demand | 0.39597 | t CaO/t SO2
Reagent consumption | 3137.5164 | t CaO/year
Reagent cost | 251001.3131 | €/year
Electricity price | 60 | €/MWh
Electricity consumption | 47974.14 | MWh/year
Electricity cost | 2878448.4 | €/year
By-product price | 20 | € / ton By-product | See reference Box 2 - by-products
By-product generated | 0.91522 | t By-product/t SO2 abated
By-product amount | 7251.9299 | t By-product/year
by-product management cost | 145038.5987 | €/year
Annual operating costs | 5171080.6373 | €/year
Summary for LSD FGD
SO2 emissions avoided | 7923.6658 | t SO2/year
Outlet SO2 concentrations obtained | 200 | mg/Nm³ SO2, dry, ref O2-%
Inlet SO2 concentrations | 728.595 | mg/Nm³ SO2, dry, ref O2-%
Efficiency | 72.5499 | %
Total investment | 127501845.7617 | €
Total annual costs | 16638736.9445 | €/year
Spec.SO2 reduction cost | 2099.8787 | €/t SO2 abated
Spec. investment per kWth | 102.0015 | €/kWth
Electricity penalty | 1.0953 | %
Share capital costs to total costs | 68.92%
Share operating costs to total costs | 31.08%
Summary for low sulphur fuel and LSD FGD
SO2 emissions avoided | 16661.0064 | t SO2/year
Outlet SO2 concentrations obtained | 200 | mg/Nm³ SO2, dry, ref O2-%
Inlet SO2 concentrations | 1311.471 | mg/Nm³ SO2, dry, ref O2-%
Efficiency | 84.7499 | %
Total investment | 127501845.7617 | €
Total annual costs | 25420794.5262 | €/year
Spec.SO2 reduction cost | 1525.7658 | €/t SO2 abated
Spec. investment per kWth | 102.0015 | €/kWth
Electricity penalty | 1.0953 | %
Share capital costs to total costs | 45.11%
Share operating costs to total costs | 54.89%
Secondary Measures - DSI FGD
DSI FGD (Y/N) | y | Y/N
SO2 emissions saved | 7923.6658 | t SO2/year |  |  |  |  | Data for calculation
Is there valorisation of waste | N | y/n |  |  |  |  | 30
Capital Costs | [6 empty] | 5
PJFF | 61626453.8305 | €
Reagent preparation unit, injection device unit cost | 18487936.1491 | € |  |  | LSFO Fixed operating cost % |  | 2.5
Total investment for DSI FGD | 80114389.9796 | €
Capital Cost p.a. | 7205576.3903 | €/year
Operating Costs
Fixed O&M Costs | 1602287.7996 | €/year
Reagent price | 80 | € / ton CaO
Specific reagent demand | 3.6682 | t CaO/t SO2
Reagent consumption | 29065.7208 | t CaO/year
Reagent cost | 2325257.6615 | €/year
Electricity price | 60 | €/MWh
Electricity consumption | 37556.8559 | MWh/year
Electricity cost (PJFF) | 2253411.3528 | €/year
By-product price | 40 | € / ton By-product
By-product generated | 8.4786 | t By-product/t SO2 abated
By-product amount | 67181.3444 | t By-product produced/year
By-product amount recovered with PJFF | 67031.4439 | t By-product recovered/year
By-product concentration (inlet FF) | 4481.7292 | mg by-product/Nm3, dry, refO2
By-product management cost | 2681257.7543 | €/year
Bag replacement cost | 1835123.1775 | €/year
Annual operating costs | 10697337.7457 | €/year
Summary for DSI FGD
SO2 emissions avoided | 7923.6658 | t SO2/year
Outlet SO2 concentrations obtained | 200 | mg/Nm³ SO2, dry, ref O2-%
Inlet SO2 concentrations | 728.595 | mg/Nm³ SO2, dry, ref O2-%
De SOx efficiency | 72.5499 | %
Total investment | 80114389.9796 | €
Total annual costs | 17902914.136 | €/year
Spec.SO2 reduction cost | 2259.4232 | €/t SO2 abated
Spec. investment per kWth | 64.0915 | €/kWth
Electricity penalty | 0.85746 | %
Share capital costs to total costs | 40.25%
Share operating costs to total costs | 59.75%
Summary for low sulphur fuel and DSI FGD
SO2 emissions avoided | 16661.0064 | t SO2/year
Outlet SO2 concentrations obtained | 200 | mg/Nm³ SO2, dry, ref O2-%
Inlet SO2 concentrations | 1311.471 | mg/Nm³ SO2, dry, ref O2-%
Efficiency | 84.7499 | %
Total investment | 80114389.9796 | €
Total annual costs | 26684971.7178 | €/year
Spec.SO2 reduction cost | 1601.6422 | €/t SO2 abated
Spec. investment per kWth | 64.0915 | €/kWth
Electricity penalty | 0.85746 | %
Share capital costs to total costs | 27%
Share operating costs to total costs | 73%
At current co-firing share
Note on C16: Not yet developed
Note on C19: By product from limestone
Note on D20: A negative figure is input due to benefit in case of valorisation, In some cases, prices even for valorisation are positive (the plant operator has to pay). In that cases, the positive prices are filled in cell D21
Note on C22: By-product from lime
Note on D23: A negative figure is input due to benefit in case of valorisation, In some cases, prices even for valorisation are positive (the plant operator has to pay). In that cases, the positive prices are filled in cell D24
Note on D27: A negative figure is input due to benefit in case of valorisation, In some cases, prices even for valorisation are positive (the plant operator has to pay). In that cases, the positive prices are filled in cell D28
Note on C29: Not yet developed
Note on D36: Choose the sulphur content of the coal
Note on O43: Examples are missing but in most cases prices are negotiated
Note on D44: You can test the 3 techniques but check your plant data and reduction efficiency required are in the range of use of the technique
Note on D47: The new SO2 outlet emissions could be taken minus 15 % of the target to take into account a margin of uncertainty
Note on D50: To be considered only for LSFO FGD and LSD FGD
Note on D74: the additional cost of the low sulphur fuel compared to the current coal, has to be included here. The 5 € per ton is for example but has to be confirmed.
Note on D215: The retrofit factor of FF is taken into account in sheet solid fuels_fabric_filter DSI (cell D83)

## Solid fuel_Fabric_Filter DSI
| Bottom up approach to define total filtration area | [8 empty] | Bottom up approach to define total filtration area - Reference Boxes
Used with DSI FGD. Do not change any parameter
Reference box PJFF0 - By-products
[10 empty] | Sale prices range from 0.35 €/t to 6 €/t. In case of disposal, price is around 3.75 €/t. |  | Questionnaires
Fly ashes can be reused for cement production and public work applications.
By-products from PJFF
| Commercial price in case of valorisation |  | €/t By-product
| By-product disposal costs |  | €/t By-product | [6 empty] | Reference box PJFF1 - Air-to-Cloth ratio
[10 empty] | Air-to-Cloth ratio (cm/s) | 1,00-2,33 | Termokimik, E-On, Enel, Balcke Durr, Lurdi, Evonik
| Which dust concentration (at stack) do you want to achieve? | [8 empty] | If PJFF is used after a dry FGD, then A/C should be in the following range : | 0,66-1,00 | Hamon
| Dust stack concentration to be obtained | 10 | mg/Nm³, O2ref, dry
| Current %-Gap to goal | 99.7769 | % | [6 empty] | Reference box PJFF2 - Conversion Net to Gross Cloth Area |  | US EPA
| Dust inlet concentration | 4481.7292 | mg/Nm³, O2ref, dry |  |  |  |  | 4471.7292 |  | Level of Net cloth Area (m²) | Multiplicator factor for gross cloth area
[8 empty] | 0.99777 |  | 0 | 2
| Air to cloth ratio for pulse jet fabric filter | [8 empty] | 370 | 1.5
| Air to cloth ratio [A/C] | 0.008 | m/s | [6 empty] | 1115 | 1.25
| Volumetric gas flow [vflue gasλ,dry] | 414.0672 | Nm³ Flue Gas,dry,λ / s | [6 empty] | 2230 | 1.17
| Net cloth area [ANC] | 51759 | m2 | [6 empty] | 3350 | 1.125
| Gross cloth area [AGC] | 53830 | m2 | [6 empty] | 4460 | 1.11
[10 empty] | 5580 | 1.1
[10 empty] | 6690 | 1.09
[10 empty] | 7810 | 1.08
[10 empty] | 8920 | 1.07
[10 empty] | 10040 | 1.06
| 1.0731e+12 | [8 empty] | 12270 | 1.05
| 2.966e+15 | [8 empty] | 16730 | 1.04
| Cost calculation | [8 empty] | Cost calculation - Reference boxes
Reference Box PJFF3 - Filter dimension
| Baghouse division | [8 empty] | Compartment division | 1-30 | Duke Energy
| Gross cloth area [AGC] | 53830 | m2 | [6 empty] | extra compartment | 0-2 | E-On, Enel
| Number of compartments | 8
| Compartment Area [Acomp] | 6728.75 | m2 | [6 empty] | Reference box PJFF4 - Price parameters for baghouse compartments - 2010 € |  |  |  | US EPA, 2002
| Number of extra compartments | 2 | [7 empty] | Baghouse type | Component | a (€) | b (€/m2)
| Total cloth area [Atot] | 67287.5 | m2 | [6 empty] | Pre-assembled unit | Basic unit | 55603.7574 | 123.5146 | Total cloth area should not exceed 2000 m² [Hamon]
[11 empty] | SS | 26789.4347 | 97.1198
[11 empty] | Insulation | 3087.6419 | 36.0565
| Cost for baghouse compartments | [8 empty] | Field assembled unit | Basic unit | 422647.4529 | 89.6696
| Compartment Area [Acomp] | 6728.75 | m2 | [7 empty] | SS | 143808.0273 | 33.9945 |  | 1
| Pre-assembled unit or field assembled unit ? | Field assembled unit | [8 empty] | Insulation | 89878.9359 | 10.037 |  | 2
| Basic unit | Y | Y
| Stainless Steel | Y | Y/N
| Thermal insulation | Y | Y/N
| a1 | 422647.4529 | €
| a2 | 143808.0273 | € | [6 empty] | Reference box PJFF5 - Bag cost factors for various materials
| a3 | 89878.9359 | € | [6 empty] | PE | 1
| b1 | 89.6696 | €/m2 | [6 empty] | CO | 1.125 | FF lesson 4
| b2 | 33.9945 | €/m2 | [6 empty] | PP | 1.2 | Balcke Durr
| b3 | 10.037 | €/m2 | [6 empty] | FG | 2.5 | FF lesson 4
| Cost for baghouse compartments | 15559760.8363 | € | [6 empty] | NO | 5 | FF lesson 4
[10 empty] | RT | 6.25 | FF lesson 4
[10 empty] | P8 | 7.5 | FF lesson 4
| Bags cost | [8 empty] | TF | 9.4 | Balcke Durr ; Entretien industriel CITEPA
| Media material | RT
| Reference price for PE material | 9 | €/m2
| Bag prices [Cbagarea] | 56.25 | €/m2 | [6 empty] | Reference Box PJFF6 - Price Utilities
| Bags cost [Cbagtotal] | 3784921.875 | € | [6 empty] | PE media price (€/m2) | 5-9
[10 empty] | Cage price (€/m2) | 16-25 | US EPA 2002
| Cage cost for pulse jet application | [8 empty] | Reference Box PJFF7 - Filter dimension
| Lenght | 8 | m | [6 empty] | Lenght (m) | 3-9 | E-On Engineering
| Diameter | 150 | mm | [6 empty] | Diameter (mm) | 120-180 | Hamon
| Cage price per m2 filtering media | 20 | €/m2 filtering media
| Total cage cost | 1345750 | €
| Economic Analysis | [8 empty] | Economic Analysis - Reference Boxes
Economic Analysis
| By product emissions avoided | 67031.4439 | t/a
| Equipment cost | 23793997.6179 | € | [6 empty] | Reference Box PJFF8 - Data Utilities
| Direct installation cost | 17607558.2373 | € | [6 empty] | Pressure drop range (mbar) | 25 - 50 | Duke Energy
| Indirect installation cost | 10707298.9281 | € | [6 empty] | Fan efficiency range (%) | 40-70 | US EPA
| Is it a new combustion plant? | N | Y/N | [6 empty] | Bag life (operating hour) | 15 000-40 000 | E-On, Enel
[10 empty] | Compressed to actual air flow ratio | 0.002 | US EPA
| Total Investment | 61626453.8305 | €
| Capital Cost p.a. | 5542751.0695 | €/a | [6 empty] | Reference Box PJFF9 - Purchase equipment factors |  | US EPA
| Operating Costs | [8 empty] | Instrumentation | 0.1
| Fixed O&M Costs | 1232529.0766 | €/a | [6 empty] | Freight | 0.05
Variable Operating Costs
| Pressure drop value | 50 | mbar
| Fan efficiency | 65% | % | [6 empty] | Reference Box PJFF10 - Direct installation factors
| Fan utility electricity consumption | 3.1693 | MWh/h | [6 empty] | Foundation & support | 0.04
| Compressed to actual air flow ratio | 0.002 | [7 empty] | Handling and erection | 0.5
| Air compressor electricity consumption | 1.118 | MWh/h | [6 empty] | Electrical | 0.08
| Bag-lifetime | 20000 | hours | [6 empty] | Piping | 0.01
| By-Product management cost | 0 | €/a | [6 empty] | Insulation for ductwork | 0.07
| Utility electricity cost | 2253411.3528 | €/a | [6 empty] | Painting | 0.04
| Bag replacement cost [Crepbags] | 1835123.1775 | €/a
| Total variable costs | 4088534.5303 | €/a | [6 empty] | Reference Box PJFF11 - Indirect installation factors
[10 empty] | Engineering | 0.1
| Summary for PJFF | [8 empty] | Construction and filed expense | 0.2
| bp emissions avoided | 67031.4439 | t bp/year | [6 empty] | Contractor fees | 0.1
| Inlet bp concentrations | 4481.7292 | mg/Nm³ bp, dry, ref O2-% | [6 empty] | Start-up | 0.01
| Outlet bp concentrations | 10 | mg/Nm³ bp, ref O2-% | [6 empty] | Performance test | 0.01
| Efficiency required | 99.7769 | % | [6 empty] | Contingencies | 0.03
| Total investment | 61626453.8305 | €
| Total annual costs | 10863814.6764 | €/year
| Spec.by reduction cost | 162.0704 | €/t bp abated
| Spec. investment per kWth | 49.3012 | €/kWth
| Electricity penalty | 0.85746 | %
| Share capital costs to total costs | 51.02%
| Share operating costs to total costs | 48.98%
Investment Data (Background Information)
| Conversion: | Conversion with currency exchange rate at given date into EUR, time conversion with CEPCI to 2010 afterwards
| Plant Electric Efficiency | 40% | Conversion kWe -> kWth
| Literature | Cost Year | Currency year / power unit |  |  |  |  | EURO 2010 / kWth
|  |  | Min | Max | Currency |  | Power unit | Min | Max
| RAINS | 2005 | 23.8 | 23.8 | £ | / | kWe | 16.3736 | 16.3736
| AEP | 2005 | 28 | 28 | £ | / | kWe | 19.263 | 19.263
| Nalbandian [Smith] | 2006 | 53 | 80 | $ | / | kWe | 18.6088 | 28.0887
| Naldandian [Orfanoudakis] | 2006 | 60.5 | 60.5 | $ | / | kWe | 21.2421 | 21.2421
| Nalbandian | 2006 | 60 | 60 | $ | / | kWe | 21.0665 | 21.0665
| World bank | 2001 | 36 | 36 | $ | / | kWe | 22.4332 | 22.4332
| IEA | 1998 | 50 | 70 | $ | / | kWe | 25.2296 | 35.3215
| Balcke Durr | 2008 | 19.7 | 21 | € | / | kWth | 18.8578 | 20.1022
| PM BART determination [American Electric Power] | 2007 | 50 | 50 | $ | / | kWe | 38.2328 | 38.2328
| Sargent et Lundy | 2010 | 65.2069 | 87.5554 | $ | / | kWe | 18.7376 | 25.1596
| IEA | 2000 | 4.8 | 45 | $ | / | kWth | 7.2603 | 68.0657
| Wu | 2001 | 3.9 | 16.5 | $ | / | kWth | 6.0803 | 25.7243
Note on D8: disposal costs or sale costs are calculated in the sheet solid fuel _deSO2
Note on D17: Cannot be changed

## Liquid fuels_DeSO2
Details on SO2 abatement techniques | [6 empty] | Details on SO2 abatement techniques - Reference Boxes
Which SO2 concentration (at stack) do you want to achieve?
SO2 stack concentration target | 200 | mg/Nm³, ref O2, dry |  |  |  |  | Reference Box 1 - reagents
Current %-Gap to goal | 87.4671 | %
Inlet SO2 concentration | 1595.8057 | mg/Nm³, ref O2, dry |  |  |  |  | CaCO3 purity may range from 90 to 98 %. From questionnaires 94 to 96 % are observed in 4 plants
Reagent and by-product charactristics and prices | [6 empty] | CaCO3 prices depend on quantity bought and quality. From questionnaires, prices range from : |  |  | Questionnaires
Purity of limestone for LSFO FGD | 96 | % | see reference box 1, reagents |  |  |  | 11 to 16 €/CaCO3 in a 2465 MWth plant and 32 to 36€/t CaCO3 in a 630 MWth plant
Price of limestone for LSFO FGD | 40 | €/t CaCO3 |  |  |  |  | and 40 €/t CaCO3 in another 630 MWth plant for similar purity of CaCO3 (94 % to 96 %)
Purity of lime for LSD FGD | 96 | %
Price of lime for LSD FGD | 80 | €/t CaO |  |  |  |  | Quicklime or CaO used in LSD FGD has a purity range from |  | 93 % is encountered | Sargent and Lundy 2007
Purity of lime for DSI FGD | 96 | % |  |  |  |  | Price is about 5 times price of limestone. Price range is 80 to 150 €/t CaO according to the specific surface
Price of lime for DSI FGD | 80 | €/t CaO |  |  |  |  | Price and purity to be completed for sodium bicarbonate
Use of Sodium bicarbonate for DSI FGF | N | Y/N
Purity of sodium bicarbonate for DSI FGD | 96 | %
Price of sodium bicarbonate for DSI FGD | 80 | €/t sodium bicarbonate
By-products from LSFO FGD | [6 empty] | Reference Box 2 - by-products |  |  |  | Reference Box 2 (following) - by-products
Commercial price in case of valorisation | -0.15 | €/t By-product | see reference box 2, by products |  |  |  | LSFO FGD: commercial-grade gypsum price depends on chlorine content, purity, colour. |  |  |  | LSD and DSI FDG:
By-product disposal (or other destination) costs | 20 | €/t By-product |  |  |  |  | Commercial grade gypsum can be used in wallboard, cement or plaster manufacturing, also soil |  |  |  | If collected separately from fly ash, in case of retrofit and use of the ESP in place, dry by-product may be
By-products from LSD FGD | [6 empty] | conditioner. Price can be low due to saturation of the market. Questionnaires provide a range between |  |  |  | land filled or used as soil conditioner.
Commercial price in case of valorisation | 0 | €/t By-product |  |  |  |  | 0.15 to 2 €/t by-product. |  |  |  | The predominant mode of dry FGD by-product elimination is disposal as fly ash separation is in fact
By-product disposal costs | 20 | €/t By-product |  |  |  |  | Disposal prices depend on the waste disposal treatment. Landfill or other treatment such as incineration. |  |  |  | rarely done.
By-products from DSI FGD | [6 empty] | By product prices range from 0.33 to 89 €/t by-product according to the questionnaires obtained. |  |  |  | According to one expert, cost for waste disposal may reach 200 €/t bp due to the fact the product is in a
From lime | [10 empty] | pulverised dry form
Commercial price in case of valorisation | 0 | €/t By-product | [8 empty] | When sold to the cement industry if the product is without fly ash, a positive cost may be encountered,
By-product disposal costs | 40 | €/t By-product | [8 empty] | 40 €/t bp
From sodium bicarbonate
Commercial price in case of valorisation
By-product disposal costs
Choice of the emission reduction technique
Primary Measures
Do you want to use a lower sulphur content fuel? | n | Yes/No | See reference box 3 - sulphur content of coals and prices
What is the sulphur content of the low sulphur fuel? | 0.5 | % Sulphur w/w waf | still provisional
Concentration achieved with low sulphur content fuel | not valid | mg/Nm³, ref O2, dry
Gap-Closure to emission goal (% of Cell D7) | n/a | %
Reduction required with secondary measure | 87.4671 | %
[7 empty] | Reference box 3 - sulphur content of fuel and prices |  |  |  | Reference box 4 - FGD efficiency and range of application
Secondary Measures | [10 empty] | LSD FGD typically used for : | plant lower than (MWth) | 1500 | Sargent and Lundy 2007
Inlet SO2 concentrations | 1595.8057 | mg/Nm³, ref O2, dry | See reference box 4 - FGD efficiency and range of application |  |  |  | Heavy fuel oil with high sulphur content (2,9%) |  | €/t |  |  | low and medium sulphur content fuels | < 1.5 % | Nalbandian 2006
Do you want to estimate costs for LSFO FGD? | Y | Yes/No |  |  |  |  | Heavy fuel oil with medium sulphur content (1,35%) |  | €/t |  | Its efficiency can reach : |  | 90 to 95 % | Sargent and Lundy 2007
Do you want to estimate costs for LSD FGD? | Y | Yes/No |  |  |  |  | Heavy fuel oil with lowsulphur content (0,9%) |  | €/t |  | LSFO FGD can be applied | for all sizes of plant but is preferably used for the largest ones |  | Sargent and Lundy 2007
Do you want to estimate costs for DSI FGD? | Y | Yes/No |  |  |  |  | Heavy fuel oil with very low sulphur content (0,5%) |  | €/t |  |  | all sulphur contents | All sulphur content
New SO2 outlet emissions | 200 | mg/Nm³, ref O2, dry | [8 empty] | Its efficiency can reach : |  | 99% | Sargent and Lundy 2007, Nalbandian 2006
Total reduction required | 87.4671 | %
Degree of Over-Achievement to ELV | 0 | % |  |  |  |  | Reference box 5 - retrofit factor
Retrofit factor | 1 |  | See reference box 5 - retrofit factor |  |  |  | retrofit factor can range from 1 to 1.4 in case of very congested site |  |  | Nalbandian 2006
| 1 |  | See reference box 3 - sulphur content of coals and prices
| heavy fouel oil Spec. Used: |  |  |  | Co-Firing Fuel Spec. Used
Lower Heating Value [LHVfuel] | 42.44 | MJ/kg LHV |  |  | Lower Heating Value [LHVfuel] | 42.44 | MJ/kg LHV
Sulphur mass fraction [xS] | 1 | % Sulphur w/w waf |  |  | Sulphur mass fraction [xS] | 1 | % Sulphur w/w waf
Ash mass fraction [xash] | 0.1 | % Ash |  |  | Ash mass fraction [xash] | 0.1 | % Ash
Moisture mass fraction [xmoist] | 0.5 | % Moisture |  |  | Moisture mass fraction [xmoist] | 0.5 | % Moisture
Spec. wet flue gas volume [vflue gasλ,wet] | 14.1552 | Nm³ Flue Gas,wet,λ /kg fuel |  |  | Spec. wet flue gas volume [vflue gasλ,wet] | 14.1552 | Nm³ Flue Gas,wet,λ /kg Fuel
Annual wet flue gas volume [vflue gasλ,wet,year] | 13147923733.7418 | Nm³ Flue Gas,wet,λ / year |  |  | Annual wet flue gas volume [vflue gasλ,wet,year] | 13147923733.7418 | Nm³ Flue Gas,wet,λ / year
Spec. dry flue gas volume [vflue gasλ,dry] | 13.0283 | Nm³ flue gas,dry,λ / kg fuel |  |  | Spec. dry flue gas volume [vflue gasλ,dry] | 13.0283 | Nm³ flue gas,dry,λ / kg Fuel
Annual dry flue gas volume [vflue gasλ,dry,year] | 12101188877.4741 | Nm³ Flue Gas,dry,λ / year |  |  | Annual dry flue gas volume [vflue gasλ,dry,year] | 12101188877.4741 | Nm³ Flue Gas,dry,λ / year
Oxygen concentration [cO2,act] | 3.8045 | % O2, dry |  |  | Oxygen concentration [cO2,act] | 3.8045 | % O2, dry
Oxygen correction factor [fO2,corr] | 1.0468 | O2 corr. Factor to ref. O2 |  |  | Oxygen correction factor [fO2,corr] | 1.0468 | O2 corr. Factor to ref. O2 %
SO2 boiler outlet emissions [loadboSO2,dry,ref O2] | 1595.8057 | mg/Nm³ SO2, dry, ref O2 |  |  | SO2 boiler outlet emissions [loadboSO2,dry,ref O2] | 1595.8057 | mg/Nm³ SO2, dry, ref O2-%
Sulphur mass fraction [x real S] | 0.994 | % Sulphur w/w real |  |  | Sulphur mass fraction [x real S] | 0.994 | % Sulphur w/w real
SO2 boiler outlet emissions [loadboSO2] | 0.46799 | kg SO2/GJ |  |  | SO2 boiler outlet emissions [loadboSO2] | 0.46799 | kg SO2/GJ
Gross heat rate [GHR] | 0.009 | GJ/kWh |  |  | Gross heat rate [GHR] | 0.009 | GJ/kWh
Economic Analysis | [6 empty] | Economic Analysis - Reference Boxes
Primary Measures - Low sulphur fuels
SO2 emissions saved | 0 | t SO2/year
Spec. Additional cost of low sulphur fuel | 5 | €/t coal | See reference box 3 - sulphur content of coals and prices
Total Investment | No investment | €
Capital Cost p.a. | No capital cost | €/year
Annual additional costs | 0 | €/year
| 0 | t fuel/year
Total annual costs | 0 | €/year
spec. SO2 reduction costs | #DIV/0! | €/t SO2
Secondary Measures - LSFO FGD (if LSFO FGD = Y)
LSFO FGD (Y/N) | Y
SO2 emissions saved | 16136.0043 | t SO2/year
Is there valorisation of waste | Y | Y/N |  |  |  |  | Reference box 6 - investment
Capital Costs | [6 empty] | Investment function derived from Sargent and Lundy 2010
Absorber unit cost | 24264943.2178 | € | see reference box 6: investment
Reagent preparation unit cost | 9126065.1162 | €
Waste handling unit cost | 4749519.3735 | €
Base balance plant cost | 46561142.5235 | €
Total cost for LSFO FGD unit | 84701670.2308 | €
Indirect installation cost | 25410501.0692 | €
Home office cost | 5505608.565 | €
Total investment cost | 115617779.8651 | €
Capital Cost p.a. | 10398790.3435 | €/year
Operating Costs | [6 empty] | Reference Box 7 - Fixed operating cost
Fixed O&M Costs | 1479985.6881 | €/year | See reference Box 7 - Fixed operating cost
[7 empty] | Fixed operating cost ratio | 2.5 | % | Sargent and Lundy 2010
Variable Operating costs
Reagent price | 40 | €/ton CaCO3 | see reference box 1, reagents
Specific limestone demand | 1.508 | t CaCO3/t SO2
Reagent consumption | 24333.5755 | t CaCO3/year
Reagent cost | 973343.0205 | €/year
Electricity price | 60 | €/MWh
Electricity consumption | 61039.68 | MWh/year
Electricity cost | 3662380.8 | €/year
By-product price | -0.15 | €/ton By-product | See reference Box 2 - by-products
By-product generated | 2.8254 | t By-product/t SO2 abated
By-product amount | 45591.3871 | t By-product/year
by-product management cost | -6838.7081 | €/year
Annual operating costs | 6108870.8006 | €/year
Summary for LSFO FGD
SO2 emissions avoided | 16136.0043 | t SO2/year
Outlet SO2 concentrations obtained | 200 | mg/Nm³ SO2, dry, ref O2-%
Inlet SO2 concentrations | 1595.8057 | mg/Nm³ SO2, dry, ref O2-%
Efficiency required | 87.4671 | %
Total investment | 115617779.8651 | €
Total annual costs | 16507661.1441 | €/year
Spec.SO2 reduction cost | 1023.0328 | €/t SO2 abated
Spec. investment per kWth | 92.4942 | €/kWth
Electricity penalty | 1.3936 | %
Share capital costs to total costs | 62.99%
Share operating costs to total costs | 37.01%
Summary for low sulphur fuel and LSFO FGD
SO2 emissions avoided | 16136.0043 | t SO2/year
Outlet SO2 concentrations obtained | 200 | mg/Nm³ SO2, dry, ref O2-%
Inlet SO2 concentrations | 1311.471 | mg/Nm³ SO2, dry, ref O2-%
Efficiency required | 84.7499 | %
Total investment | 115617779.8651 | €
Total annual costs | 16507661.1441 | €/year
Spec.SO2 reduction cost | 1023.0328 | €/t SO2 abated
Spec. investment per kWth | 92.4942 | €/kWth
Electricity penalty | 1.3936 | %
Share capital costs to total costs | 62.99%
Share operating costs to total costs | 37.01%
Secondary Measures - LSD FGD (if LSD FGD = Y)
LSD FGD (Y/N) | Y | Y/N
SO2 emissions saved | 16136.0043 | t SO2/year
Is there valorisation of waste | N | y/n
Capital Costs
Absorber unit cost | 24949891.4708 | € | see reference box 6: investment
Reagent preparation and waste handling units cost | 14517903.9317 | €
Base balance plant cost | 36834004.9449 | €
Total cost for LSD FGD unit | 76301800.3474 | €
Indirect installation cost | 22890540.1042 | €
Home office cost | 4959617.0226 | €
Total investment cost | 104151957.4742 | €
Capital Cost p.a. | 9367541.661 | €/year
Operating Costs
Fixed O&M Costs | 1549262.3032 | €/year | See reference Box 7 - Fixed operating cost
Reagent price | 80 | € / ton CaO | see reference box 1, reagents
Specific reagent demand | 1.3842 | t CaO/t SO2
Reagent consumption | 22335.5164 | t CaO/year
Reagent cost | 1786841.3153 | €/year
Electricity price | 60 | €/MWh
Electricity consumption | 47974.14 | MWh/year
Electricity cost | 2878448.4 | €/year
By-product price | 20 | € / ton By-product | See reference Box 2 - by-products
By-product generated | 3.1994 | t By-product/t SO2 abated
By-product amount | 51625.4193 | t By-product/year
by-product management cost | 1032508.3856 | €/year
Annual operating costs | 7247060.4041 | €/year
Summary for LSD FGD
SO2 emissions avoided | 16136.0043 | t SO2/year
Outlet SO2 concentrations obtained | 200 | mg/Nm³ SO2, dry, ref O2-%
Inlet SO2 concentrations | 1595.8057 | mg/Nm³ SO2, dry, ref O2-%
Efficiency | 87.4671 | %
Total investment | 104151957.4742 | €
Total annual costs | 16614602.0652 | €/year
Spec.SO2 reduction cost | 1029.6602 | €/t SO2 abated
Spec. investment per kWth | 83.3216 | €/kWth
Electricity penalty | 1.0953 | %
Share capital costs to total costs | 56.38%
Share operating costs to total costs | 43.62%
Summary for low sulphur fuel and LSD FGD
SO2 emissions avoided | 16136.0043 | t SO2/year
outlet SO2 concentrations obtained | 200 | mg/Nm³ SO2, dry, ref O2-%
inlet SO2 concentrations | 1311.471 | mg/Nm³ SO2, dry, ref O2-%
Efficiency | 84.7499 | %
Total investment | 104151957.4742 | €
Total annual costs | 16614602.0652 | €/year
Spec.SO2 reduction cost | 1029.6602 | €/t SO2 abated
Spec. investment per kWth | 83.3216 | €/kWth
Electricity penalty | 1.0953 | %
Share capital costs to total costs | 56.38%
Share operating costs to total costs | 43.62%
Secondary Measures - DSI FGD
DSI FGD (Y/N) | Y | Y/N
SO2 emissions saved | 16136.0043 | t SO2/year |  |  |  | Data for calculation
Is there valorisation of waste | N | y/n |  |  |  | 30
Capital Costs | [5 empty] | 5
PJFF | 43404493.7175 | €
Reagent preparation unit, injection device unit cost | 13021348.1153 | € |  | LSFO Fixed operating cost % |  | 2.5
Total investment for DSI FGD | 56425841.8328 | €
Capital Cost p.a. | 5075002.3038 | €/year
Operating Costs
Fixed O&M Costs | 1128516.8367 | €/year
Reagent price | 80 | € / ton CaO
Specific reagent demand | 4.6879 | t CaO/t SO2
Reagent consumption | 75644.7717 | t CaO/year
Reagent cost | 6051581.7334 | €/year
Electricity price | 60 | €/MWh
Electricity consumption | 34804.8545 | MWh/year
Electricity cost (PJFF) | 2088291.2727 | €/year
By-product price | 40 | € / ton By-product
By-product generated | 10.8355 | t By-product/t SO2 abated
By-product amount | 174842.2994 | t By-product produced/year
By-product amount recovered with PJFF | 174726.6959 | t By-product recovered/year
By-product concentration (inlet FF) | 15124.3064 | mg by-product/Nm3, dry, refO2
By-product management cost | 6989067.837 | €/year
Bag replacement cost | 1835123.1775 | €/year
Annual operating costs | 18092580.8572 | €/year
Summary for DSI FGD
SO2 emissions avoided | 16136.0043 | t SO2/year
Outlet SO2 concentrations obtained | 200 | mg/Nm³ SO2, dry, ref O2-%
Inlet SO2 concentrations | 1595.8057 | mg/Nm³ SO2, dry, ref O2-%
De SOx efficiency | 87.4671 | %
Total investment | 56425841.8328 | €
Total annual costs | 23167583.161 | €/year
Spec.SO2 reduction cost | 1435.7695 | €/t SO2 abated
Spec. investment per kWth | 45.1407 | €/kWth
Electricity penalty | 0.79463 | %
Share capital costs to total costs | 21.91%
Share operating costs to total costs | 78.09%
Summary for low sulphur fuel and DSI FGD
SO2 emissions avoided | 16136.0043 | t SO2/year
Outlet SO2 concentrations obtained | 200 | mg/Nm³ SO2, dry, ref O2-%
Inlet SO2 concentrations | 1311.471 | mg/Nm³ SO2, dry, ref O2-%
Efficiency | 84.7499 | %
Total investment | 56425841.8328 | €
Total annual costs | 23167583.161 | €/year
Spec.SO2 reduction cost | 1435.7695 | €/t SO2 abated
Spec. investment per kWth | 45.1407 | €/kWth
Electricity penalty | 0.79463 | %
Share capital costs to total costs | 21.91%
Share operating costs to total costs | 78.09%
At current co-firing share
Note on C16: Not yet developed
Note on C19: By product from limestone
Note on D20: A negative figure is input due to benefit in case of valorisation, In some cases, prices even for valorisation are positive (the plant operator has to pay). In that cases, the positive prices are filled in cell D21
Note on C22: By-product from lime
Note on D23: A negative figure is input due to benefit in case of valorisation, In some cases, prices even for valorisation are positive (the plant operator has to pay). In that cases, the positive prices are filled in cell D24
Note on D27: A negative figure is input due to benefit in case of valorisation, In some cases, prices even for valorisation are positive (the plant operator has to pay). In that cases, the positive prices are filled in cell D28
Note on C29: Not yet developed
Note on D36: Choose the sulphur content of the fuel
Note on O43: to be filled, examples missing.
Note on D44: You can test the 3 techniques but check your plant data and reduction efficiency required are in the range of use of the technique
Note on D47: The new SO2 outlet emissions could be taken minus 15 % of the target to take into account a margin of uncertainty
Note on D50: To be considered only for LSFO FGD and LSD FGD
Note on D74: the additional cost of the low sulphur fuel compared to the current coal, has to be included here. 5 e is just ised as example.
Note on D215: The retrofit factor of FF is taken into account in sheet solid fuels_fabric_filter DSI (cell D83)

## Liquid fuel_Fabric_Filter DSI
| Bottom up approach to define total filtration area | [8 empty] | Bottom up approach to define total filtration area - Reference Boxes
Used with DSI FGD. Do not change any parameter
Reference box PJFF0 - By-products
[10 empty] | Sale prices range from 0.35 €/t to 6 €/t. In case of disposal, price is around 3.75 €/t. |  | Questionnaires
Fly ashes can be reused for cement production and public work applications.
By-products from PJFF
| Commercial price in case of valorisation |  | €/t By-product
| By-product disposal costs |  | €/t By-product | [6 empty] | Reference box PJFF1 - Air-to-Cloth ratio
[10 empty] | Air-to-Cloth ratio (cm/s) | 1,00-2,33 | Termokimik, E-On, Enel, Balcke Durr, Lurdi, Evonik
| Which dust concentration (at stack) do you want to achieve? | [8 empty] | If PJFF is used after a dry FGD, then A/C should be in the following range : | 0,66-1,00 | Hamon
| Dust stack concentration to be obtained | 10 | mg/Nm³, O2ref, dry
| Current %-Gap to goal | 99.9339 | % | [6 empty] | Reference box PJFF2 - Conversion Net to Gross Cloth Area |  | US EPA
| Dust inlet concentration | 15124.3064 | mg/Nm³, O2ref, dry | [6 empty] | Level of Net cloth Area (m²) | Multiplicator factor for gross cloth area
[10 empty] | 0 | 2
| Air to cloth ratio for pulse jet fabric filter | [8 empty] | 370 | 1.5
| Air to cloth ratio [A/C] | 0.008 | m/s | [6 empty] | 1115 | 1.25
| Volumetric gas flow [vflue gasλ,dry] | 383.7262 | Nm³ Flue Gas,dry,λ / s | [6 empty] | 2230 | 1.17
| Net cloth area [ANC] | 47966 | m2 | [6 empty] | 3350 | 1.125
| Gross cloth area [AGC] | 49885 | m2 | [6 empty] | 4460 | 1.11
[10 empty] | 5580 | 1.1
[10 empty] | 6690 | 1.09
[10 empty] | 7810 | 1.08
[10 empty] | 8920 | 1.07
[10 empty] | 10040 | 1.06
[10 empty] | 12270 | 1.05
[10 empty] | 16730 | 1.04
| Cost calculation | [8 empty] | Cost calculation - Reference boxes
Reference Box PJFF3 - Filter dimension
| Baghouse division | [8 empty] | Compartment division | 1-30 | Duke Energy
| Gross cloth area [AGC] | 49885 | m2 | [6 empty] | extra compartment | 0-2 | E-On, Enel
| Number of compartments | 8
| Compartment Area [Acomp] | 6235.625 | m2 | [6 empty] | Reference box PJFF4 - Price parameters for baghouse compartments - 2010 € |  |  |  | US EPA, 2002
| Number of extra compartments | 2 | [7 empty] | Baghouse type | Component | a (€) | b (€/m2)
| Total cloth area [Atot] | 62356.25 | m2 | [6 empty] | Pre-assembled unit | Basic unit | 55603.7574 | 123.5146 | Total cloth area should not exceed 2000 m² [Hamon]
[11 empty] | SS | 26789.4347 | 97.1198
[11 empty] | Insulation | 3087.6419 | 36.0565
| Cost for baghouse compartments | [8 empty] | Field assembled unit | Basic unit | 422647.4529 | 89.6696
| Compartment Area [Acomp] | 6235.625 | m2 | [7 empty] | SS | 143808.0273 | 33.9945 |  | 1
| Pre-assembled unit or field assembled unit ? | Field assembled unit | [8 empty] | Insulation | 89878.9359 | 10.037 |  | 2
| Basic unit | Y | Y
| Stainless Steel | N | Y/N
| Thermal insulation | N | Y/N
| a1 | 422647.4529 | €
| a2 | 0 | € | [6 empty] | Reference box PJFF5 - Bag cost factors for various materials
| a3 | 0 | € | [6 empty] | PE | 1
| b1 | 89.6696 | €/m2 | [6 empty] | CO | 1.125 | FF lesson 4
| b2 | 0 | €/m2 | [6 empty] | PP | 1.2 | Balcke Durr
| b3 | 0 | €/m2 | [6 empty] | FG | 2.5 | FF lesson 4
| Cost for baghouse compartments | 9817937.4878 | € | [6 empty] | NO | 5 | FF lesson 4
[10 empty] | RT | 6.25 | FF lesson 4
[10 empty] | P8 | 7.5 | FF lesson 4
| Bags cost | [8 empty] | TF | 9.4 | Balcke Durr ; Entretien industriel CITEPA
| Media material | RT
| Reference price for PE material | 9 | €/m2
| Bag prices [Cbagarea] | 56.25 | €/m2 | [6 empty] | Reference Box PJFF6 - Price Utilities
| Bags cost [Cbagtotal] | 3507539.0625 | € | [6 empty] | PE media price (€/m2) | 5-9
[10 empty] | Cage price (€/m2) | 16-25 | US EPA 2002
| Cage cost for pulse jet application | [8 empty] | Reference Box PJFF7 - Filter dimension
| Lenght | 8 | m | [6 empty] | Lenght (m) | 3-9 | E-On Engineering
| Diameter | 150 | mm | [6 empty] | Diameter (mm) | 120-180 | Hamon
| Cage price per m2 | 20 | €/m2
| Total cage cost | 1247125 | €
| Economic Analysis | [8 empty] | Economic Analysis - Reference Boxes
Economic Analysis
| By product emissions avoided | 174726.6959 | t/a
| Equipment cost | 16758491.7828 | € | [6 empty] | Reference Box PJFF8 - Data Utilities
| Direct installation cost | 12401283.9193 | € | [6 empty] | Pressure drop range (mbar) | 25 - 50 | Duke Energy
| Indirect installation cost | 7541321.3023 | € | [6 empty] | Fan efficiency range (%) | 40-70 | US EPA
| Is it a new combustion plant? | N | Y/N | [6 empty] | Bag life (operating hour) | 15 000-40 000 | E-On, Enel
[10 empty] | Compressed to actual air flow ratio | 0.002 | US EPA
| Total Investment | 43404493.7175 | €
| Capital Cost p.a. | 3903847.926 | €/a | [6 empty] | Reference Box PJFF9 - Purchase equipment factors |  | US EPA
| Operating Costs | [8 empty] | Instrumentation | 0.1
| Fixed O&M Costs | 868089.8744 | €/a | [6 empty] | Freight | 0.05
Variable Operating Costs
| Pressure drop value | 50 | mbar
| Fan efficiency | 65% | % | [6 empty] | Reference Box PJFF10 - Direct installation factors
| Fan utility electricity consumption | 2.9371 | MWh/h | [6 empty] | Foundation & support | 0.04
| Compressed to actual air flow ratio | 0.002 | [7 empty] | Handling and erection | 0.5
| Air compressor electricity consumption | 1.0361 | MWh/h | [6 empty] | Electrical | 0.08
| Bag-lifetime | 20000 | hours | [6 empty] | Piping | 0.01
| By-Product management cost | 0 | €/a | [6 empty] | Insulation for ductwork | 0.07
| Utility electricity cost | 2088291.2727 | €/a | [6 empty] | Painting | 0.04
| Bag replacement cost [Crepbags] | 1700633.8419 | €/a
| Total variable costs | 3788925.1146 | €/a | [6 empty] | Reference Box PJFF11 - Indirect installation factors
[10 empty] | Engineering | 0.1
| Summary for PJFF | [8 empty] | Construction and filed expense | 0.2
| bp emissions avoided | 174726.6959 | t bp/year | [6 empty] | Contractor fees | 0.1
| Inlet bp concentrations | 15124.3064 | mg/Nm³ bp, dry, ref O2-% | [6 empty] | Start-up | 0.01
| Outlet bp concentrations | 10 | mg/Nm³ bp, ref O2-% | [6 empty] | Performance test | 0.01
| Efficiency required | 99.9339 | % | [6 empty] | Contingencies | 0.03
| Total investment | 43404493.7175 | €
| Total annual costs | 8560862.9149 | €/year
| Spec.TSP reduction cost | 48.9957 | €/t bp abated
| Spec. investment per kWth | 34.7236 | €/kWth
| Electricity penalty | 0.79463 | %
| Share capital costs to total costs | 45.6%
| Share operating costs to total costs | 54.4%
Investment Data (Background Information)
| Conversion: | Conversion with currency exchange rate at given date into EUR, time conversion with CEPCI to 2010 afterwards
| Plant Electric Efficiency | 40% | Conversion kWe -> kWth
| Literature | Cost Year | Currency year / power unit |  |  |  |  | EURO 2010 / kWth
|  |  | Min | Max | Currency |  | Power unit | Min | Max
| RAINS | 2005 | 23.8 | 23.8 | £ | / | kWe | 16.3736 | 16.3736
| AEP | 2005 | 28 | 28 | £ | / | kWe | 19.263 | 19.263
| Nalbandian [Smith] | 2006 | 53 | 80 | $ | / | kWe | 18.6088 | 28.0887
| Naldandian [Orfanoudakis] | 2006 | 60.5 | 60.5 | $ | / | kWe | 21.2421 | 21.2421
| Nalbandian | 2006 | 60 | 60 | $ | / | kWe | 21.0665 | 21.0665
| World bank | 2001 | 36 | 36 | $ | / | kWe | 22.4332 | 22.4332
| IEA | 1998 | 50 | 70 | $ | / | kWe | 25.2296 | 35.3215
| Balcke Durr | 2008 | 19.7 | 21 | € | / | kWth | 18.8578 | 20.1022
| PM BART determination [American Electric Power] | 2007 | 50 | 50 | $ | / | kWe | 38.2328 | 38.2328
| Sargent et Lundy | 2010 | 65.2069 | 87.5554 | $ | / | kWe | 18.7376 | 25.1596
| IEA | 2000 | 4.8 | 45 | $ | / | kWth | 7.2603 | 68.0657
| Wu | 2001 | 3.9 | 16.5 | $ | / | kWth | 6.0803 | 25.7243
Note on D8: disposal costs or sale costs are calculated in the sheet solid fuel _deSO2
Note on D17: Cannot be changed
Note on D97: in sheet liquid fuel SO2

## SUIVI
Modification made on the file | Date of modification |  | Who
addition of FGD LSFO and LSD | 10/10 and 14/10 |  | NA
last changes by jean-baptiste on | 2013-10-10 |  | JBV
including NOX for liquid and gaseous fuels | 2013-10-14 |  | AKM SSB
Correction of retrofit calculation ESP and PJFF | 2013-10-16 |  | JBV
Correction of name definition in PJFF sheet | 2013-10-16 |  | JBV
Input factor for the test for coal | 2013-10-24 |  | NA
small changes on some sheets | 2013-10-30 |  | AKM SSB
addition of DSI FGD and correction of some | 2013-10-31 |  | NA
cells in sheet ESP for liquid fuels | 2013-10-31 |  | NA
addition of by-product management for dedusters | 2013-10-31 |  | NA
Correction Calculation of O2-Correction Factor | 2013-11-04 |  | SSB
Change Liq-Fuels Emission Calculation wet/dry spec. Flue gas | 2013-11-04 |  | SSB
correction following the CEFIC meeting | 2013-11-06 |  | SSB
correction following the CEFIC meeting | 2013-11-08 |  | NA
changes made all pointed in red for explanations | 2013-11-09 |  | NA
Corrections AKM et SS | 2013-11-12 |  | AKM SSB
aditions NA | 2013-11-14 |  | NA
Changes for Dry FGD | 2013-11-18 |  | NA
Correction of equation 4-12 in fabric filter sheet | 2014-02-12 |  | JBV
Correction on sheet solid fuels_fabric _filter | 2014-05-28 |  | NA
line 11 emission replaced by concentration
line 12 emission replaced by concentration
line 42 colour blue
line 83 Is it a new PJFF unit? Replaced by it is a new combustion plant?
Line 88 : C40 eliminated
line 96 life by lifetime
D47-47-50 and 51 modification of the equation as the change in the choice SS or insulation was not working
Correction on sheet solid fuels_ESP
line 8 emission replaced by concentration
line 9 emission replaced by concentration
line 46 Is it a new PJFF unit? Replaced by it is a new combustion plant?
Correction on sheet liquid fuels_ESP
line 8 emission replaced by concentration
line 9 emission replaced by concentration
line 46 Is it a new PJFF unit? Replaced by it is a new combustion plant?
Solid_fuels_DeSO2
line 5 emission replaced by concentration
line 6 emission replaced by concentration
lines 9 addition of characteristics
line 92 Total cost for LSFO FGD unit
c170 lime instead of limestone
Line 158
Correction sur D193 et D207 (n'allaient pas prendre D79)
Solid_fuels_fabric_filter_DSI
line 11 emission replaced by concentration
line 12 emission replaced by concentration
line 42 colour blue
line 83 Is it a new PJFF unit? Replaced by it is a new combustion plant?
line 96 life by lifetime
D47-47-50 and 51 modification of the equation as the change in the choice SS or insulation was not working
Liquid_fuels_DeSO2
line 5 emission replaced by concentration
line 6 emission replaced by concentration
lines 9 addition of characteristics
line 74 coal replaced by fuel
line 92 Total cost for LSFO FGD unit
Line 158
c170 et C229 reagent instead of limestone
Cell D38 link to the solid fuel sheet replaced by the liquid fuel sheet
Correction sur D191, 192, 193, 207, 125, 126, 225, 252, 253
Liquid_fuels_fabric_filter_DSI
line 11 emission replaced by concentration
line 12 emission replaced by concentration
line 42 colour blue
line 83 Is it a new PJFF unit? Replaced by it is a new combustion plant?
line 96 life by lifetime
correction link sur D111, 112, 87
D47-47-50 and 51 modification of the equation as the change in the choice SS or insulation was not working
| 2014-06-11 | NA
Solid fuels - Nox Analysis
O84 blue replaced by green
O87 blue replaced by green
Liquid fuels - Nox Analysis
O84 blue replaced by green
O87 blue replaced by green
Gaseous fuels
O84 blue replaced by green
O87 blue replaced by green
Solid fuels - Nox Analysis | 2014-06-12 | CM AKM
N72: "SR" replaced by "Stoichiometric Ratio"
N77: "P.D." replaced by "Pressure Drop"
Liquid fuels - Nox Analysis
N72: "SR" replaced by "Stoichiometric Ratio"
N77: "P.D." replaced by "Pressure Drop"
Natural Gas - Nox Analysis
N72: "SR" replaced by "Stoichiometric Ratio"
N77: "P.D." replaced by "Pressure Drop"
Solid fuels - emission calc.
line 71, 79: blue color adapted to the same blue as used in the rest of the document
Natural gas - emission calc.
C51: COAL replaced by GAS
line 42-43: new lines inserted to have identical cell numbers for the description in the manual (compared to solid and liquid fuels)
line 67: blue color adapted to the same blue as used in the rest of the document
Solid fuels - Nox Analysis | 13.06. | CM AKM
Liquid fuels - Nox Analysis
Natural Gas - Nox Analysis
D59 and D85: orange to blue
NA 01/10/2014
in sheet solid fuels_deSO2, cell D235 is modified the link is done with cell D 213 instead of D149
in sheet liquid fuels_deSO2, cell D235 is modified the link is done with cell D 213 instead of D150
cell D42 of sheets solid fuel_fabric_filter_DSI in blue
cell D42 of sheets Liquid fuel_fabric_filter_DSI in blue
Formulas:
Date of modification = [Date of modification, row above]